## README
ADICOT ENGINEERING — HVAC Equipment Selection Database
INDOOR FAN COILS
FG5_Cooling_Cap | FG5 fan coil gross cooling capacities vs CFM, EWB, Sat Leaving Evap Temp (SST). Used with GA5SAN5/GA8TAN5 condensing units.
FJ5_Cooling_Cap | FJ5 fan coil gross cooling capacities vs CFM, EWB, SST. Used with GH5SAN5/GH8TAN5 heat pumps and GA5SAN5 A/C.
FG5_Airflow | FG5 nominal CFM by fan coil size and matched outdoor unit capacity.
FJ5_Airflow | FJ5 CFM vs tap and external static pressure.
SHC_Correction | Sensible heat capacity correction for entering DB != 80F. Formula: CF = 1.09 x (1-BF) x (DB-80)
OUTDOOR — A/C ONLY
GA5_Condenser_Only | GA5SAN5 single-stage condensing unit gross cooling capacity (TCG), SDT, kW vs SST and outdoor DB. KEY selection table.
GA8_Condenser_Only | GA8TAN5 2-stage condensing unit (High stage and Low stage) same format.
GA5_Detail_Cool | GA5SAN5 net cooling capacities matched with CVAVA indoor coils — reference/cross-check only.
GA8_Detail_Cool | GA8TAN5 net cooling capacities (High/Low) — reference/cross-check only.
OUTDOOR — HEAT PUMPS
GH5_Detail_Cool | GH5SAN5 single-stage HP net cooling capacities vs CFM, EWB, Outdoor DB. Paired with FJ5 indoor units.
GH8_Detail_Cool | GH8TAN5 2-stage HP net cooling capacities (High/Low) vs CFM, EWB, Outdoor DB. Paired with FG5 indoor units.
GH5_Heating | GH5SAN5 heating performance vs EDB, CFM, Outdoor DB (-3 to 67F). Integrated values (defrost subtracted).
GH8_Heating | GH8TAN5 heating performance (High/Low) vs EDB, CFM, Outdoor DB (-3 to 57F+).
MATCHING RULES
Valid_Combinations | Allowed indoor/outdoor pairings by nominal tonnage.
SELECTION LOGIC NOTES
A/C selection (GA5/GA8): | 1) Pick CFM from FG5/FJ5 airflow table for matched ODU size. 2) Compute indoor EWB from inputs. 3) Iterate SST: find intersection where indoor coil TC = condenser TCG. 4) Filter to 100-115% of zone load.
HP cooling selection (GH5/GH8): | Direct interpolation in GH5_Detail_Cool / GH8_Detail_Cool tables using CFM, EWB, outdoor DB.
HP heating check: | Interpolate GH5_Heating / GH8_Heating at design heating outdoor DB, EDB=70, CFM. Compare to heating load if provided.
Sensible check: | Corrected SHC = table SHC +/- (1.09 x (1-BF) x (EDB-80) x CFM/1000). Must meet zone sensible load.

## FG5_Cooling_Cap
FC_Size | CFM | EWB_F | SST_F | TC_kBtu | SHC_kBtu | BF | Source: FG5 Product Data Table 10 — Cooling Capacities (MBtuh). SHC based on 80F EDB.
24 | 525 | 72 | 35 | 37.43 | 19.02 | 0
24 | 525 | 72 | 40 | 34 | 17.19 | 0
24 | 525 | 72 | 45 | 30.1 | 15.23 | 0
24 | 525 | 72 | 50 | 25.65 | 13.15 | 0
24 | 525 | 72 | 55 | 20.64 | 10.99 | 0
24 | 525 | 67 | 35 | 30.69 | 19.43 | 0
24 | 525 | 67 | 40 | 27.12 | 17.47 | 0
24 | 525 | 67 | 45 | 23.06 | 15.4 | 0
24 | 525 | 67 | 50 | 18.59 | 13.27 | 0
24 | 525 | 67 | 55 | 13.61 | 11.08 | 0
24 | 525 | 62 | 35 | 24.56 | 19.7 | 0
24 | 525 | 62 | 40 | 20.93 | 17.68 | 0
24 | 525 | 62 | 45 | 16.97 | 15.6 | 0.01
24 | 525 | 62 | 50 | 12.99 | 12.89 | 0.02
24 | 525 | 62 | 55 | 10.73 | 10.73 | 0.18
24 | 700 | 72 | 35 | 46.22 | 23.43 | 0
24 | 700 | 72 | 40 | 42.1 | 21.33 | 0
24 | 700 | 72 | 45 | 37.38 | 19.05 | 0
24 | 700 | 72 | 50 | 31.94 | 16.6 | 0
24 | 700 | 72 | 55 | 25.66 | 13.94 | 0
24 | 700 | 67 | 35 | 38.17 | 24.4 | 0.01
24 | 700 | 67 | 40 | 33.83 | 22.11 | 0.01
24 | 700 | 67 | 45 | 28.81 | 19.63 | 0
24 | 700 | 67 | 50 | 23.12 | 16.95 | 0.01
24 | 700 | 67 | 55 | 16.96 | 14.3 | 0.01
24 | 700 | 62 | 35 | 30.7 | 25.11 | 0.01
24 | 700 | 62 | 40 | 26.21 | 22.68 | 0.01
24 | 700 | 62 | 45 | 21.31 | 20.14 | 0.01
24 | 700 | 62 | 50 | 16.75 | 16.75 | 0.05
24 | 700 | 62 | 55 | 13.97 | 13.97 | 0.2
24 | 875 | 72 | 35 | 53.39 | 27.09 | 0
24 | 875 | 72 | 40 | 48.7 | 24.8 | 0
24 | 875 | 72 | 45 | 43.3 | 22.29 | 0
24 | 875 | 72 | 50 | 37.16 | 19.57 | 0.01
24 | 875 | 72 | 55 | 29.96 | 16.59 | 0.01
24 | 875 | 67 | 35 | 44.26 | 28.66 | 0.01
24 | 875 | 67 | 40 | 39.35 | 26.15 | 0.01
24 | 875 | 67 | 45 | 33.65 | 23.41 | 0.01
24 | 875 | 67 | 50 | 27.11 | 20.38 | 0.02
24 | 875 | 67 | 55 | 19.88 | 17.29 | 0.02
24 | 875 | 62 | 35 | 35.9 | 29.97 | 0.02
24 | 875 | 62 | 40 | 30.79 | 27.25 | 0.02
24 | 875 | 62 | 45 | 25.2 | 24.36 | 0.03
24 | 875 | 62 | 50 | 20.34 | 20.34 | 0.08
24 | 875 | 62 | 55 | 16.99 | 16.99 | 0.23
24 | 1050 | 72 | 35 | 59.25 | 30.19 | 0
24 | 1050 | 72 | 40 | 54.13 | 27.79 | 0
24 | 1050 | 72 | 45 | 48.25 | 25.09 | 0.01
24 | 1050 | 72 | 50 | 41.43 | 22.16 | 0.02
24 | 1050 | 72 | 55 | 33.6 | 18.95 | 0.02
24 | 1050 | 67 | 35 | 49.32 | 32.39 | 0.02
24 | 1050 | 67 | 40 | 43.94 | 29.71 | 0.03
24 | 1050 | 67 | 45 | 37.72 | 26.76 | 0.03
24 | 1050 | 67 | 50 | 30.51 | 23.51 | 0.03
24 | 1050 | 67 | 55 | 22.41 | 20.04 | 0.03
24 | 1050 | 62 | 35 | 40.19 | 34.31 | 0.03
24 | 1050 | 62 | 40 | 34.71 | 31.44 | 0.03
24 | 1050 | 62 | 45 | 28.63 | 28.3 | 0.04
24 | 1050 | 62 | 50 | 23.57 | 23.57 | 0.11
24 | 1050 | 62 | 55 | 19.71 | 19.71 | 0.25
24 | 1225 | 72 | 35 | 64.13 | 32.86 | 0.01
24 | 1225 | 72 | 40 | 58.72 | 30.36 | 0.02
24 | 1225 | 72 | 45 | 52.4 | 27.56 | 0.03
24 | 1225 | 72 | 50 | 45.06 | 24.47 | 0.03
24 | 1225 | 72 | 55 | 36.56 | 21.07 | 0.03
24 | 1225 | 67 | 35 | 53.55 | 35.72 | 0.04
24 | 1225 | 67 | 40 | 47.8 | 32.91 | 0.04
24 | 1225 | 67 | 45 | 41.11 | 29.81 | 0.04
24 | 1225 | 67 | 50 | 33.4 | 26.4 | 0.04
24 | 1225 | 67 | 55 | 24.73 | 22.69 | 0.05
24 | 1225 | 62 | 35 | 43.83 | 38.28 | 0.04
24 | 1225 | 62 | 40 | 38.03 | 35.26 | 0.04
24 | 1225 | 62 | 45 | 31.7 | 31.95 | 0.05
24 | 1225 | 62 | 50 | 26.61 | 26.61 | 0.14
24 | 1225 | 62 | 55 | 22.21 | 22.21 | 0.28
36 | 700 | 72 | 35 | 43.33 | 22.33 | 0
36 | 700 | 72 | 40 | 39.24 | 20.2 | 0
36 | 700 | 72 | 45 | 34.54 | 17.9 | 0
36 | 700 | 72 | 50 | 29.27 | 15.5 | 0
36 | 700 | 72 | 55 | 23.32 | 12.96 | 0
36 | 700 | 67 | 35 | 35.55 | 23.09 | 0.01
36 | 700 | 67 | 40 | 31.29 | 20.81 | 0.01
36 | 700 | 67 | 45 | 26.53 | 18.39 | 0.01
36 | 700 | 67 | 50 | 21.15 | 15.88 | 0.01
36 | 700 | 67 | 55 | 15.36 | 13.31 | 0.01
36 | 700 | 62 | 35 | 28.5 | 23.7 | 0.01
36 | 700 | 62 | 40 | 24.22 | 21.35 | 0.01
36 | 700 | 62 | 45 | 19.63 | 18.93 | 0.02
36 | 700 | 62 | 50 | 15.45 | 15.45 | 0.05
36 | 700 | 62 | 55 | 12.83 | 12.83 | 0.21
36 | 875 | 72 | 35 | 50.29 | 25.92 | 0
36 | 875 | 72 | 40 | 45.6 | 23.58 | 0
36 | 875 | 72 | 45 | 40.23 | 21.05 | 0
36 | 875 | 72 | 50 | 34.05 | 18.28 | 0.01
36 | 875 | 72 | 55 | 27.07 | 15.39 | 0
36 | 875 | 67 | 35 | 41.42 | 27.22 | 0.01
36 | 875 | 67 | 40 | 36.53 | 24.66 | 0.02
36 | 875 | 67 | 45 | 30.93 | 21.9 | 0.02
36 | 875 | 67 | 50 | 24.68 | 19.03 | 0.02
36 | 875 | 67 | 55 | 17.98 | 16.12 | 0.02
36 | 875 | 62 | 35 | 33.3 | 28.27 | 0.02
36 | 875 | 62 | 40 | 28.43 | 25.63 | 0.02
36 | 875 | 62 | 45 | 23.2 | 22.9 | 0.03
36 | 875 | 62 | 50 | 18.76 | 18.76 | 0.08
36 | 875 | 62 | 55 | 15.6 | 15.59 | 0.24
36 | 1050 | 72 | 35 | 55.99 | 28.96 | 0
36 | 1050 | 72 | 40 | 50.88 | 26.52 | 0
36 | 1050 | 72 | 45 | 44.98 | 23.76 | 0.01
36 | 1050 | 72 | 50 | 38.16 | 20.78 | 0.02
36 | 1050 | 72 | 55 | 30.32 | 17.54 | 0.02
36 | 1050 | 67 | 35 | 46.35 | 30.86 | 0.02
36 | 1050 | 67 | 40 | 40.94 | 28.11 | 0.03
36 | 1050 | 67 | 45 | 34.65 | 25.09 | 0.03
36 | 1050 | 67 | 50 | 27.71 | 21.92 | 0.03
36 | 1050 | 67 | 55 | 20.29 | 18.7 | 0.03
36 | 1050 | 62 | 35 | 37.45 | 32.47 | 0.03
36 | 1050 | 62 | 40 | 32.02 | 29.55 | 0.03
36 | 1050 | 62 | 45 | 26.34 | 26.56 | 0.04
36 | 1050 | 62 | 50 | 21.73 | 21.73 | 0.12
36 | 1050 | 62 | 55 | 18.08 | 18.08 | 0.26
36 | 1225 | 72 | 35 | 60.74 | 31.57 | 0.01
36 | 1225 | 72 | 40 | 55.32 | 29.01 | 0.02
36 | 1225 | 72 | 45 | 49.03 | 26.17 | 0.03
36 | 1225 | 72 | 50 | 41.65 | 23.01 | 0.03
36 | 1225 | 72 | 55 | 33.08 | 19.54 | 0.03
36 | 1225 | 67 | 35 | 50.52 | 34.11 | 0.04
36 | 1225 | 67 | 40 | 44.7 | 31.22 | 0.04
36 | 1225 | 67 | 45 | 37.94 | 28.03 | 0.04
36 | 1225 | 67 | 50 | 30.3 | 24.61 | 0.04
36 | 1225 | 67 | 55 | 22.35 | 21.12 | 0.05
36 | 1225 | 62 | 35 | 41.02 | 36.3 | 0.04
36 | 1225 | 62 | 40 | 35.23 | 33.22 | 0.04
36 | 1225 | 62 | 45 | 29.16 | 29.97 | 0.06
36 | 1225 | 62 | 50 | 24.47 | 24.47 | 0.15
36 | 1225 | 62 | 55 | 20.38 | 20.37 | 0.29
36 | 1400 | 72 | 35 | 64.78 | 33.88 | 0.03
36 | 1400 | 72 | 40 | 59.07 | 31.25 | 0.03
36 | 1400 | 72 | 45 | 52.43 | 28.31 | 0.04
36 | 1400 | 72 | 50 | 44.65 | 25.02 | 0.04
36 | 1400 | 72 | 55 | 35.54 | 21.38 | 0.04
36 | 1400 | 67 | 35 | 54.04 | 37.04 | 0.05
36 | 1400 | 67 | 40 | 47.93 | 34.06 | 0.05
36 | 1400 | 67 | 45 | 40.78 | 30.74 | 0.05
36 | 1400 | 67 | 50 | 32.59 | 27.1 | 0.05
36 | 1400 | 67 | 55 | 24.21 | 23.4 | 0.06
36 | 1400 | 62 | 35 | 44.12 | 39.84 | 0.05
36 | 1400 | 62 | 40 | 38.06 | 36.62 | 0.06
36 | 1400 | 62 | 45 | 31.77 | 33.15 | 0.08
36 | 1400 | 62 | 50 | 27 | 27 | 0.18
36 | 1400 | 62 | 55 | 22.51 | 22.51 | 0.32
48 | 875 | 72 | 35 | 57.42 | 29.42 | 0
48 | 875 | 72 | 40 | 52.45 | 26.85 | 0
48 | 875 | 72 | 45 | 46.71 | 24.03 | 0
48 | 875 | 72 | 50 | 40.18 | 21.03 | 0
48 | 875 | 72 | 55 | 32.63 | 17.8 | 0
48 | 875 | 67 | 35 | 47.42 | 30.6 | 0
48 | 875 | 67 | 40 | 42.24 | 27.82 | 0
48 | 875 | 67 | 45 | 36.26 | 24.83 | 0
48 | 875 | 67 | 50 | 29.43 | 21.6 | 0
48 | 875 | 67 | 55 | 21.78 | 18.21 | 0
48 | 875 | 62 | 35 | 38.36 | 31.59 | 0
48 | 875 | 62 | 40 | 32.96 | 28.62 | 0
48 | 875 | 62 | 45 | 26.96 | 25.49 | 0.01
48 | 875 | 62 | 50 | 21.02 | 21.02 | 0.03
48 | 875 | 62 | 55 | 17.57 | 17.57 | 0.19
48 | 1050 | 72 | 35 | 64.85 | 33.22 | 0
48 | 1050 | 72 | 40 | 59.39 | 30.49 | 0
48 | 1050 | 72 | 45 | 53.01 | 27.45 | 0
48 | 1050 | 72 | 50 | 45.54 | 24.1 | 0
48 | 1050 | 72 | 55 | 37.03 | 20.53 | 0
48 | 1050 | 67 | 35 | 53.78 | 35.04 | 0
48 | 1050 | 67 | 40 | 47.89 | 31.97 | 0
48 | 1050 | 67 | 45 | 41.2 | 28.7 | 0
48 | 1050 | 67 | 50 | 33.53 | 25.1 | 0.01
48 | 1050 | 67 | 55 | 24.88 | 21.33 | 0.01
48 | 1050 | 62 | 35 | 43.59 | 36.53 | 0.01
48 | 1050 | 62 | 40 | 37.61 | 33.29 | 0.01
48 | 1050 | 62 | 45 | 30.92 | 29.84 | 0.01
48 | 1050 | 62 | 50 | 24.69 | 24.69 | 0.05
48 | 1050 | 62 | 55 | 20.68 | 20.68 | 0.2
48 | 1225 | 72 | 35 | 71.17 | 36.52 | 0
48 | 1225 | 72 | 40 | 65.31 | 33.68 | 0
48 | 1225 | 72 | 45 | 58.44 | 30.5 | 0
48 | 1225 | 72 | 50 | 50.32 | 26.94 | 0
48 | 1225 | 72 | 55 | 40.86 | 23.04 | 0
48 | 1225 | 67 | 35 | 59.24 | 39.03 | 0.01
48 | 1225 | 67 | 40 | 52.9 | 35.81 | 0.01
48 | 1225 | 67 | 45 | 45.53 | 32.24 | 0.01
48 | 1225 | 67 | 50 | 37.13 | 28.38 | 0.01
48 | 1225 | 67 | 55 | 27.69 | 24.29 | 0.01
48 | 1225 | 62 | 35 | 48.2 | 41.12 | 0.01
48 | 1225 | 62 | 40 | 41.7 | 37.66 | 0.01
48 | 1225 | 62 | 45 | 34.53 | 33.97 | 0.02
48 | 1225 | 62 | 50 | 28.2 | 28.2 | 0.07
48 | 1225 | 62 | 55 | 23.64 | 23.64 | 0.22
48 | 1400 | 72 | 35 | 76.52 | 39.42 | 0
48 | 1400 | 72 | 40 | 70.39 | 36.54 | 0
48 | 1400 | 72 | 45 | 63.1 | 33.25 | 0
48 | 1400 | 72 | 50 | 54.49 | 29.55 | 0
48 | 1400 | 72 | 55 | 44.24 | 25.33 | 0.01
48 | 1400 | 67 | 35 | 63.96 | 42.66 | 0.01
48 | 1400 | 67 | 40 | 57.26 | 39.33 | 0.01
48 | 1400 | 67 | 45 | 49.36 | 35.56 | 0.01
48 | 1400 | 67 | 50 | 40.3 | 31.47 | 0.01
48 | 1400 | 67 | 55 | 30.25 | 27.12 | 0.02
48 | 1400 | 62 | 35 | 52.27 | 45.42 | 0.02
48 | 1400 | 62 | 40 | 45.32 | 41.79 | 0.02
48 | 1400 | 62 | 45 | 37.86 | 37.9 | 0.03
48 | 1400 | 62 | 50 | 31.5 | 31.5 | 0.09
48 | 1400 | 62 | 55 | 26.46 | 26.46 | 0.24
48 | 1600 | 72 | 35 | 81.7 | 42.36 | 0
48 | 1600 | 72 | 40 | 75.29 | 39.42 | 0
48 | 1600 | 72 | 45 | 67.76 | 36.07 | 0.01
48 | 1600 | 72 | 50 | 58.64 | 32.2 | 0.01
48 | 1600 | 72 | 55 | 47.74 | 27.81 | 0.01
48 | 1600 | 67 | 35 | 68.59 | 46.44 | 0.02
48 | 1600 | 67 | 40 | 61.56 | 43.01 | 0.02
48 | 1600 | 67 | 45 | 53.21 | 39.12 | 0.02
48 | 1600 | 67 | 50 | 43.5 | 34.78 | 0.02
48 | 1600 | 67 | 55 | 32.89 | 30.19 | 0.03
48 | 1600 | 62 | 35 | 56.34 | 50 | 0.02
48 | 1600 | 62 | 40 | 49.07 | 46.2 | 0.03
48 | 1600 | 62 | 45 | 41.28 | 42.13 | 0.04
48 | 1600 | 62 | 50 | 34.99 | 34.99 | 0.12
48 | 1600 | 62 | 55 | 29.45 | 29.45 | 0.26
48 | 1750 | 72 | 35 | 85.08 | 44.35 | 0.01
48 | 1750 | 72 | 40 | 78.5 | 41.36 | 0.01
48 | 1750 | 72 | 45 | 70.73 | 37.98 | 0.01
48 | 1750 | 72 | 50 | 61.36 | 34.06 | 0.02
48 | 1750 | 72 | 55 | 50.07 | 29.56 | 0.02
48 | 1750 | 67 | 35 | 71.64 | 49.07 | 0.02
48 | 1750 | 67 | 40 | 64.38 | 45.58 | 0.02
48 | 1750 | 67 | 45 | 55.79 | 41.62 | 0.02
48 | 1750 | 67 | 50 | 45.66 | 37.13 | 0.03
48 | 1750 | 67 | 55 | 34.67 | 32.39 | 0.04
48 | 1750 | 62 | 35 | 59.05 | 53.24 | 0.03
48 | 1750 | 62 | 40 | 51.63 | 49.36 | 0.03
48 | 1750 | 62 | 45 | 43.66 | 45.12 | 0.05
48 | 1750 | 62 | 50 | 37.41 | 37.41 | 0.14
48 | 1750 | 62 | 55 | 31.54 | 31.54 | 0.28
60 | 1050 | 72 | 35 | 76.72 | 37.31 | 0
60 | 1050 | 72 | 40 | 70.53 | 34.32 | 0
60 | 1050 | 72 | 45 | 63.26 | 31 | 0
60 | 1050 | 72 | 50 | 54.72 | 27.31 | 0
60 | 1050 | 72 | 55 | 44.87 | 23.33 | 0
60 | 1050 | 67 | 35 | 63.75 | 39.28 | 0
60 | 1050 | 67 | 40 | 57.04 | 35.92 | 0
60 | 1050 | 67 | 45 | 49.37 | 32.29 | 0
60 | 1050 | 67 | 50 | 40.47 | 28.33 | 0
60 | 1050 | 67 | 55 | 30.31 | 24.09 | 0
60 | 1050 | 62 | 35 | 51.77 | 40.86 | 0
60 | 1050 | 62 | 40 | 44.85 | 37.28 | 0
60 | 1050 | 62 | 45 | 36.98 | 33.42 | 0
60 | 1050 | 62 | 50 | 29.15 | 29.15 | 0.03
60 | 1050 | 62 | 55 | 24.49 | 24.49 | 0.18
60 | 1225 | 72 | 35 | 84.49 | 41.13 | 0
60 | 1225 | 72 | 40 | 77.85 | 38.03 | 0
60 | 1225 | 72 | 45 | 70.02 | 34.53 | 0
60 | 1225 | 72 | 50 | 60.74 | 30.62 | 0
60 | 1225 | 72 | 55 | 49.75 | 26.24 | 0
60 | 1225 | 67 | 35 | 70.49 | 43.87 | 0
60 | 1225 | 67 | 40 | 63.25 | 40.34 | 0
60 | 1225 | 67 | 45 | 54.75 | 36.39 | 0
60 | 1225 | 67 | 50 | 44.98 | 32.11 | 0
60 | 1225 | 67 | 55 | 33.84 | 27.49 | 0.01
60 | 1225 | 62 | 35 | 57.45 | 46.11 | 0.01
60 | 1225 | 62 | 40 | 49.84 | 42.26 | 0
60 | 1225 | 62 | 45 | 41.36 | 38.12 | 0.01
60 | 1225 | 62 | 50 | 33.38 | 33.38 | 0.05
60 | 1225 | 62 | 55 | 28.07 | 28.07 | 0.2
60 | 1400 | 72 | 35 | 91.12 | 44.48 | 0
60 | 1400 | 72 | 40 | 84.15 | 41.32 | 0
60 | 1400 | 72 | 45 | 75.88 | 37.72 | 0
60 | 1400 | 72 | 50 | 66 | 33.63 | 0
60 | 1400 | 72 | 55 | 54.14 | 28.99 | 0
60 | 1400 | 67 | 35 | 76.32 | 48.04 | 0.01
60 | 1400 | 67 | 40 | 68.68 | 44.39 | 0
60 | 1400 | 67 | 45 | 59.63 | 40.25 | 0.01
60 | 1400 | 67 | 50 | 48.99 | 35.66 | 0.01
60 | 1400 | 67 | 55 | 37.06 | 30.73 | 0.01
60 | 1400 | 62 | 35 | 62.46 | 51.03 | 0.01
60 | 1400 | 62 | 40 | 54.28 | 46.94 | 0.01
60 | 1400 | 62 | 45 | 45.37 | 42.59 | 0.01
60 | 1400 | 62 | 50 | 37.36 | 37.36 | 0.07
60 | 1400 | 62 | 55 | 31.5 | 31.5 | 0.22
60 | 1600 | 72 | 35 | 97.58 | 47.87 | 0
60 | 1600 | 72 | 40 | 90.26 | 44.66 | 0
60 | 1600 | 72 | 45 | 81.63 | 41 | 0
60 | 1600 | 72 | 50 | 71.22 | 36.77 | 0
60 | 1600 | 72 | 55 | 58.6 | 31.93 | 0
60 | 1600 | 67 | 35 | 82.11 | 52.42 | 0.01
60 | 1600 | 67 | 40 | 74.04 | 48.65 | 0.01
60 | 1600 | 67 | 45 | 64.49 | 44.38 | 0.01
60 | 1600 | 67 | 50 | 53.05 | 39.51 | 0.01
60 | 1600 | 67 | 55 | 40.39 | 34.28 | 0.02
60 | 1600 | 62 | 35 | 67.5 | 56.28 | 0.01
60 | 1600 | 62 | 40 | 58.97 | 52.08 | 0.01
60 | 1600 | 62 | 45 | 49.59 | 47.46 | 0.02
60 | 1600 | 62 | 50 | 41.69 | 41.69 | 0.1
60 | 1600 | 62 | 55 | 35.23 | 35.23 | 0.23
60 | 1750 | 72 | 35 | 101.79 | 50.2 | 0
60 | 1750 | 72 | 40 | 94.24 | 46.95 | 0
60 | 1750 | 72 | 45 | 85.37 | 43.24 | 0
60 | 1750 | 72 | 50 | 74.69 | 38.94 | 0.01
60 | 1750 | 72 | 55 | 61.65 | 33.96 | 0.01
60 | 1750 | 67 | 35 | 85.85 | 55.43 | 0.01
60 | 1750 | 67 | 40 | 77.59 | 51.63 | 0.01
60 | 1750 | 67 | 45 | 67.69 | 47.28 | 0.01
60 | 1750 | 67 | 50 | 55.89 | 42.3 | 0.01
60 | 1750 | 67 | 55 | 42.67 | 36.85 | 0.02
60 | 1750 | 62 | 35 | 70.88 | 60.02 | 0.02
60 | 1750 | 62 | 40 | 62.2 | 55.73 | 0.02
60 | 1750 | 62 | 45 | 52.49 | 50.96 | 0.03
60 | 1750 | 62 | 50 | 44.77 | 44.77 | 0.11
60 | 1750 | 62 | 55 | 37.9 | 37.9 | 0.25
60 | 2000 | 72 | 35 | 107.82 | 53.69 | 0.01
60 | 2000 | 72 | 40 | 99.99 | 50.42 | 0.01
60 | 2000 | 72 | 45 | 90.79 | 46.63 | 0.01
60 | 2000 | 72 | 50 | 79.66 | 42.29 | 0.01
60 | 2000 | 72 | 55 | 66.02 | 37.13 | 0.01
60 | 2000 | 67 | 35 | 91.23 | 60.09 | 0.02
60 | 2000 | 67 | 40 | 82.69 | 56.25 | 0.02
60 | 2000 | 67 | 45 | 72.42 | 51.79 | 0.02
60 | 2000 | 67 | 50 | 60.17 | 46.63 | 0.02
60 | 2000 | 67 | 55 | 46.16 | 40.91 | 0.03
60 | 2000 | 62 | 35 | 75.82 | 65.87 | 0.02
60 | 2000 | 62 | 40 | 66.93 | 61.51 | 0.03
60 | 2000 | 62 | 45 | 57.16 | 56.55 | 0.04
60 | 2000 | 62 | 50 | 49.51 | 49.51 | 0.14
60 | 2000 | 62 | 55 | 42.03 | 42.03 | 0.27

## FJ5_Cooling_Cap
FC_Size | CFM | EWB_F | SST_F | TC_kBtu | SHC_kBtu | BF
18 | 525 | 72 | 35 | 42.8 | 20.8 | 0
18 | 525 | 72 | 40 | 38.4 | 18.7 | 0
18 | 525 | 72 | 45 | 33.5 | 16.5 | 0.01
18 | 525 | 72 | 50 | 27.9 | 14.1 | 0.02
18 | 525 | 72 | 55 | 21.7 | 11.7 | 0.02
18 | 525 | 67 | 35 | 34.9 | 21.4 | 0.03
18 | 525 | 67 | 40 | 30.4 | 19.2 | 0.03
18 | 525 | 67 | 45 | 25.3 | 16.8 | 0.03
18 | 525 | 67 | 50 | 19.8 | 14.5 | 0.03
18 | 525 | 67 | 55 | 13.9 | 12.1 | 0.04
18 | 525 | 62 | 35 | 27.7 | 21.9 | 0.03
18 | 525 | 62 | 40 | 23.2 | 19.6 | 0.03
18 | 525 | 62 | 45 | 18.5 | 17.3 | 0.04
18 | 525 | 62 | 50 | 14.9 | 14.9 | 0.13
18 | 525 | 62 | 55 | 12.2 | 12.2 | 0.28
18 | 600 | 72 | 35 | 46.9 | 22.8 | 0
18 | 600 | 72 | 40 | 42.1 | 20.5 | 0
18 | 600 | 72 | 45 | 36.7 | 18.1 | 0.02
18 | 600 | 72 | 50 | 30.6 | 15.6 | 0.03
18 | 600 | 72 | 55 | 23.8 | 13 | 0.03
18 | 600 | 67 | 35 | 38.3 | 23.7 | 0.04
18 | 600 | 67 | 40 | 33.4 | 21.2 | 0.04
18 | 600 | 67 | 45 | 27.8 | 18.7 | 0.04
18 | 600 | 67 | 50 | 21.6 | 16.1 | 0.04
18 | 600 | 67 | 55 | 15.2 | 13.4 | 0.05
18 | 600 | 62 | 35 | 30.4 | 24.3 | 0.04
18 | 600 | 62 | 40 | 25.4 | 21.8 | 0.04
18 | 600 | 62 | 45 | 20.3 | 19.3 | 0.06
18 | 600 | 62 | 50 | 16.5 | 16.5 | 0.15
18 | 600 | 62 | 55 | 13.6 | 13.6 | 0.3
18 | 675 | 72 | 35 | 50.6 | 24.6 | 0
18 | 675 | 72 | 40 | 45.4 | 22.2 | 0.02
18 | 675 | 72 | 45 | 39.6 | 19.7 | 0.03
18 | 675 | 72 | 50 | 33 | 17 | 0.04
18 | 675 | 72 | 55 | 25.6 | 14.1 | 0.04
18 | 675 | 67 | 35 | 41.4 | 25.7 | 0.05
18 | 675 | 67 | 40 | 36.1 | 23.1 | 0.05
18 | 675 | 67 | 45 | 30.1 | 20.4 | 0.05
18 | 675 | 67 | 50 | 23.4 | 17.6 | 0.05
18 | 675 | 67 | 55 | 16.5 | 14.8 | 0.06
18 | 675 | 62 | 35 | 32.9 | 26.6 | 0.05
18 | 675 | 62 | 40 | 27.5 | 23.9 | 0.05
18 | 675 | 62 | 45 | 22.1 | 21.1 | 0.07
18 | 675 | 62 | 50 | 18.1 | 18.1 | 0.17
18 | 675 | 62 | 55 | 14.9 | 14.9 | 0.32
24 | 700 | 72 | 35 | 54.4 | 26.4 | 0
24 | 700 | 72 | 40 | 49.2 | 24 | 0
24 | 700 | 72 | 45 | 43.3 | 21.4 | 0.01
24 | 700 | 72 | 50 | 36.4 | 18.5 | 0.02
24 | 700 | 72 | 55 | 28.6 | 15.5 | 0.03
24 | 700 | 67 | 35 | 44.8 | 27.7 | 0.03
24 | 700 | 67 | 40 | 39.3 | 25 | 0.03
24 | 700 | 67 | 45 | 33 | 22.1 | 0.03
24 | 700 | 67 | 50 | 26 | 19.1 | 0.03
24 | 700 | 67 | 55 | 18.5 | 16.1 | 0.04
24 | 700 | 62 | 35 | 35.8 | 28.6 | 0.03
24 | 700 | 62 | 40 | 30.2 | 25.8 | 0.03
24 | 700 | 62 | 45 | 24.3 | 22.9 | 0.04
24 | 700 | 62 | 50 | 19.7 | 19.7 | 0.13
24 | 700 | 62 | 55 | 16.3 | 16.3 | 0.28
24 | 800 | 72 | 35 | 59.1 | 28.7 | 0
24 | 800 | 72 | 40 | 53.5 | 26.2 | 0.01
24 | 800 | 72 | 45 | 47 | 23.4 | 0.02
24 | 800 | 72 | 50 | 39.7 | 20.3 | 0.03
24 | 800 | 72 | 55 | 31.2 | 31.2 | 0.04
24 | 800 | 67 | 35 | 48.7 | 30.4 | 0.04
24 | 800 | 67 | 40 | 42.9 | 27.6 | 0.04
24 | 800 | 67 | 45 | 36.1 | 24.5 | 0.04
24 | 800 | 67 | 50 | 28.3 | 21.2 | 0.04
24 | 800 | 67 | 55 | 20.2 | 17.9 | 0.05
24 | 800 | 62 | 35 | 39.1 | 31.6 | 0.04
24 | 800 | 62 | 40 | 33 | 28.6 | 0.05
24 | 800 | 62 | 45 | 26.6 | 25.4 | 0.06
24 | 800 | 62 | 50 | 21.9 | 21.9 | 0.16
24 | 800 | 62 | 55 | 18.1 | 18.1 | 0.3
24 | 900 | 72 | 35 | 63.2 | 30.8 | 0
24 | 900 | 72 | 40 | 57.2 | 28.2 | 0.02
24 | 900 | 72 | 45 | 50.4 | 25.2 | 0.04
24 | 900 | 72 | 50 | 42.6 | 22 | 0.04
24 | 900 | 72 | 55 | 33.5 | 18.6 | 0.05
24 | 900 | 67 | 35 | 52.3 | 32.8 | 0.05
24 | 900 | 67 | 40 | 46.1 | 29.9 | 0.05
24 | 900 | 67 | 45 | 38.9 | 26.7 | 0.05
24 | 900 | 67 | 50 | 30.5 | 23.2 | 0.05
24 | 900 | 67 | 55 | 21.8 | 19.6 | 0.06
24 | 900 | 62 | 35 | 42.1 | 34.5 | 0.05
24 | 900 | 62 | 40 | 35.6 | 31.3 | 0.06
24 | 900 | 62 | 45 | 28.8 | 27.9 | 0.07
24 | 900 | 62 | 50 | 24 | 24 | 0.18
24 | 900 | 62 | 55 | 19.8 | 19.8 | 0.32
30 | 875 | 72 | 35 | 71.6 | 34.7 | 0
30 | 875 | 72 | 40 | 64.4 | 31.3 | 0
30 | 875 | 72 | 45 | 56.3 | 27.7 | 0
30 | 875 | 72 | 50 | 47.2 | 23.8 | 0.02
30 | 875 | 72 | 55 | 36.8 | 19.7 | 0.02
30 | 875 | 67 | 35 | 58.7 | 36 | 0.02
30 | 875 | 67 | 40 | 51.3 | 32.3 | 0.03
30 | 875 | 67 | 45 | 42.9 | 28.4 | 0.03
30 | 875 | 67 | 50 | 33.6 | 24.4 | 0.03
30 | 875 | 67 | 55 | 23.7 | 20.3 | 0.04
30 | 875 | 62 | 35 | 46.7 | 36.8 | 0.03
30 | 875 | 62 | 40 | 39.2 | 33 | 0.03
30 | 875 | 62 | 45 | 31.2 | 29.1 | 0.04
30 | 875 | 62 | 50 | 25 | 25 | 0.12
30 | 875 | 62 | 55 | 20.6 | 20.6 | 0.27
30 | 1000 | 72 | 35 | 78.3 | 38 | 0
30 | 1000 | 72 | 40 | 70.5 | 34.4 | 0
30 | 1000 | 72 | 45 | 61.6 | 30.5 | 0.02
30 | 1000 | 72 | 50 | 51.7 | 26.3 | 0.03
30 | 1000 | 72 | 55 | 40.3 | 21.9 | 0.03
30 | 1000 | 67 | 35 | 64.3 | 39.7 | 0.03
30 | 1000 | 67 | 40 | 56.3 | 35.8 | 0.03
30 | 1000 | 67 | 45 | 47.1 | 31.5 | 0.04
30 | 1000 | 67 | 50 | 36.8 | 27.1 | 0.04
30 | 1000 | 67 | 55 | 26 | 22.7 | 0.05
30 | 1000 | 62 | 35 | 51.4 | 40.9 | 0.04
30 | 1000 | 62 | 40 | 43.1 | 36.7 | 0.04
30 | 1000 | 62 | 45 | 34.4 | 32.4 | 0.05
30 | 1000 | 62 | 50 | 27.9 | 27.9 | 0.14
30 | 1000 | 62 | 55 | 23 | 23 | 0.29
30 | 1125 | 72 | 35 | 84.3 | 41 | 0
30 | 1125 | 72 | 40 | 75.9 | 37.2 | 0
30 | 1125 | 72 | 45 | 66.8 | 33.2 | 0.02
30 | 1125 | 72 | 50 | 55.8 | 28.6 | 0.04
30 | 1125 | 72 | 55 | 43.6 | 23.8 | 0.04
30 | 1125 | 67 | 35 | 69.4 | 43.1 | 0.04
30 | 1125 | 67 | 40 | 60.8 | 38.9 | 0.04
30 | 1125 | 67 | 45 | 51 | 34.5 | 0.05
30 | 1125 | 67 | 50 | 39.8 | 29.7 | 0.05
30 | 1125 | 67 | 55 | 28.1 | 24.9 | 0.06
30 | 1125 | 62 | 35 | 55.6 | 44.8 | 0.05
30 | 1125 | 62 | 40 | 46.7 | 40.3 | 0.05
30 | 1125 | 62 | 45 | 37.3 | 35.6 | 0.06
30 | 1125 | 62 | 50 | 30.6 | 30.6 | 0.16
30 | 1125 | 62 | 55 | 25.2 | 25.2 | 0.31
36 | 1050 | 72 | 35 | 64.89 | 33.39 | 0
36 | 1050 | 72 | 40 | 58.38 | 30.18 | 0
36 | 1050 | 72 | 45 | 51.08 | 26.68 | 0.02
36 | 1050 | 72 | 50 | 42.84 | 22.99 | 0.03
36 | 1050 | 72 | 55 | 33.4 | 19.04 | 0.03
36 | 1050 | 67 | 35 | 53.14 | 34.96 | 0.04
36 | 1050 | 67 | 40 | 46.48 | 31.47 | 0.04
36 | 1050 | 67 | 45 | 38.88 | 27.72 | 0.04
36 | 1050 | 67 | 50 | 30.22 | 23.74 | 0.04
36 | 1050 | 67 | 55 | 21.13 | 19.74 | 0.05
36 | 1050 | 62 | 35 | 42.35 | 36.18 | 0.04
36 | 1050 | 62 | 40 | 35.45 | 32.44 | 0.04
36 | 1050 | 62 | 45 | 28.12 | 28.54 | 0.05
36 | 1050 | 62 | 50 | 22.73 | 22.73 | 0.15
36 | 1050 | 62 | 55 | 18.64 | 18.64 | 0.29
36 | 1200 | 72 | 35 | 70.55 | 36.42 | 0
36 | 1200 | 72 | 40 | 63.54 | 32.99 | 0.02
36 | 1200 | 72 | 45 | 55.62 | 29.26 | 0.03
36 | 1200 | 72 | 50 | 46.67 | 25.3 | 0.04
36 | 1200 | 72 | 55 | 36.48 | 21.08 | 0.05
36 | 1200 | 67 | 35 | 57.9 | 38.43 | 0.05
36 | 1200 | 67 | 40 | 50.7 | 34.71 | 0.05
36 | 1200 | 67 | 45 | 42.55 | 30.74 | 0.05
36 | 1200 | 67 | 50 | 33.13 | 26.44 | 0.05
36 | 1200 | 67 | 55 | 23.14 | 22.04 | 0.06
36 | 1200 | 62 | 35 | 46.31 | 40.09 | 0.05
36 | 1200 | 62 | 40 | 38.86 | 36.09 | 0.05
36 | 1200 | 62 | 45 | 31.02 | 31.87 | 0.07
36 | 1200 | 62 | 50 | 25.31 | 25.31 | 0.17
36 | 1200 | 62 | 55 | 20.78 | 20.78 | 0.31
36 | 1350 | 72 | 35 | 75.52 | 39.17 | 0
36 | 1350 | 72 | 40 | 68.14 | 35.55 | 0.03
36 | 1350 | 72 | 45 | 59.7 | 31.64 | 0.04
36 | 1350 | 72 | 50 | 50.12 | 27.45 | 0.05
36 | 1350 | 72 | 55 | 39.26 | 23 | 0.06
36 | 1350 | 67 | 35 | 62.18 | 41.63 | 0.06
36 | 1350 | 67 | 40 | 54.49 | 37.72 | 0.06
36 | 1350 | 67 | 45 | 45.77 | 33.52 | 0.06
36 | 1350 | 67 | 50 | 35.75 | 28.98 | 0.06
36 | 1350 | 67 | 55 | 25 | 24.22 | 0.08
36 | 1350 | 62 | 35 | 49.84 | 43.73 | 0.06
36 | 1350 | 62 | 40 | 42 | 39.53 | 0.07
36 | 1350 | 62 | 45 | 33.71 | 35.01 | 0.09
36 | 1350 | 62 | 50 | 27.74 | 27.74 | 0.2
36 | 1350 | 62 | 55 | 22.79 | 22.79 | 0.33
42 | 1225 | 72 | 35 | 79.15 | 40.41 | 0
42 | 1225 | 72 | 40 | 70.85 | 36.31 | 0
42 | 1225 | 72 | 45 | 61.59 | 31.9 | 0.02
42 | 1225 | 72 | 50 | 51.15 | 27.24 | 0.03
42 | 1225 | 72 | 55 | 39.41 | 22.38 | 0.04
42 | 1225 | 67 | 35 | 64.55 | 42.04 | 0.04
42 | 1225 | 67 | 40 | 56.05 | 37.58 | 0.04
42 | 1225 | 67 | 45 | 46.51 | 32.9 | 0.04
42 | 1225 | 67 | 50 | 35.85 | 28.04 | 0.04
42 | 1225 | 67 | 55 | 24.9 | 23.25 | 0.05
42 | 1225 | 62 | 35 | 51.09 | 43.18 | 0.04
42 | 1225 | 62 | 40 | 42.46 | 38.53 | 0.05
42 | 1225 | 62 | 45 | 33.59 | 33.84 | 0.06
42 | 1225 | 62 | 50 | 27.05 | 27.05 | 0.15
42 | 1225 | 62 | 55 | 22.11 | 22.11 | 0.3
42 | 1400 | 72 | 35 | 86.34 | 44.2 | 0
42 | 1400 | 72 | 40 | 77.3 | 39.79 | 0.01
42 | 1400 | 72 | 45 | 67.22 | 35.05 | 0.03
42 | 1400 | 72 | 50 | 55.91 | 30.07 | 0.04
42 | 1400 | 72 | 55 | 43.1 | 24.8 | 0.05
42 | 1400 | 67 | 35 | 70.55 | 46.3 | 0.05
42 | 1400 | 67 | 40 | 61.37 | 41.55 | 0.05
42 | 1400 | 67 | 45 | 50.95 | 36.5 | 0.05
42 | 1400 | 67 | 50 | 39.2 | 31.18 | 0.06
42 | 1400 | 67 | 55 | 27.27 | 25.94 | 0.07
42 | 1400 | 62 | 35 | 56.04 | 47.92 | 0.06
42 | 1400 | 62 | 40 | 46.63 | 42.89 | 0.06
42 | 1400 | 62 | 45 | 36.98 | 37.71 | 0.08
42 | 1400 | 62 | 50 | 30.12 | 30.12 | 0.18
42 | 1400 | 62 | 55 | 24.63 | 24.62 | 0.32
42 | 1575 | 72 | 35 | 92.81 | 47.68 | 0
42 | 1575 | 72 | 40 | 83.15 | 42.98 | 0.03
42 | 1575 | 72 | 45 | 72.31 | 37.96 | 0.05
42 | 1575 | 72 | 50 | 60.17 | 32.67 | 0.06
42 | 1575 | 72 | 55 | 46.45 | 27.07 | 0.06
42 | 1575 | 67 | 35 | 76 | 50.25 | 0.06
42 | 1575 | 67 | 40 | 66.13 | 45.22 | 0.06
42 | 1575 | 67 | 45 | 55.01 | 39.88 | 0.07
42 | 1575 | 67 | 50 | 42.37 | 34.2 | 0.07
42 | 1575 | 67 | 55 | 29.47 | 28.5 | 0.08
42 | 1575 | 62 | 35 | 60.57 | 52.4 | 0.07
42 | 1575 | 62 | 40 | 50.47 | 47.01 | 0.07
42 | 1575 | 62 | 45 | 40.22 | 41.43 | 0.09
42 | 1575 | 62 | 50 | 33.01 | 33.01 | 0.2
42 | 1575 | 62 | 55 | 26.99 | 26.99 | 0.34
48 | 1400 | 72 | 35 | 83.95 | 44.3 | 0
48 | 1400 | 72 | 40 | 75.71 | 40.05 | 0
48 | 1400 | 72 | 45 | 66.36 | 35.45 | 0.01
48 | 1400 | 72 | 50 | 55.84 | 30.58 | 0.02
48 | 1400 | 72 | 55 | 43.82 | 25.38 | 0.03
48 | 1400 | 67 | 35 | 68.8 | 46.22 | 0.03
48 | 1400 | 67 | 40 | 60.32 | 41.61 | 0.03
48 | 1400 | 67 | 45 | 50.67 | 36.7 | 0.03
48 | 1400 | 67 | 50 | 39.64 | 31.45 | 0.03
48 | 1400 | 67 | 55 | 27.8 | 26.12 | 0.04
48 | 1400 | 62 | 35 | 54.96 | 47.71 | 0.03
48 | 1400 | 62 | 40 | 46.12 | 42.77 | 0.03
48 | 1400 | 62 | 45 | 36.69 | 37.67 | 0.04
48 | 1400 | 62 | 50 | 29.32 | 29.32 | 0.13
48 | 1400 | 62 | 55 | 24.1 | 24.1 | 0.28
48 | 1600 | 72 | 35 | 91.53 | 48.4 | 0
48 | 1600 | 72 | 40 | 82.59 | 43.9 | 0
48 | 1600 | 72 | 45 | 72.47 | 38.97 | 0.02
48 | 1600 | 72 | 50 | 61.02 | 33.73 | 0.03
48 | 1600 | 72 | 55 | 48.01 | 28.16 | 0.04
48 | 1600 | 67 | 35 | 75.19 | 50.91 | 0.04
48 | 1600 | 67 | 40 | 65.98 | 45.99 | 0.04
48 | 1600 | 67 | 45 | 55.57 | 40.75 | 0.04
48 | 1600 | 67 | 50 | 43.57 | 35.09 | 0.04
48 | 1600 | 67 | 55 | 30.49 | 29.21 | 0.05
48 | 1600 | 62 | 35 | 60.21 | 52.94 | 0.04
48 | 1600 | 62 | 40 | 50.73 | 47.68 | 0.04
48 | 1600 | 62 | 45 | 40.48 | 42.1 | 0.06
48 | 1600 | 62 | 50 | 32.72 | 32.72 | 0.15
48 | 1600 | 62 | 55 | 26.92 | 26.92 | 0.3
48 | 1800 | 72 | 35 | 98.31 | 52.15 | 0
48 | 1800 | 72 | 40 | 88.79 | 47.39 | 0.02
48 | 1800 | 72 | 45 | 77.99 | 42.21 | 0.03
48 | 1800 | 72 | 50 | 65.7 | 36.65 | 0.04
48 | 1800 | 72 | 55 | 51.81 | 30.76 | 0.05
48 | 1800 | 67 | 35 | 80.94 | 55.25 | 0.05
48 | 1800 | 67 | 40 | 71.1 | 50.06 | 0.05
48 | 1800 | 67 | 45 | 59.93 | 44.5 | 0.05
48 | 1800 | 67 | 50 | 47.14 | 38.52 | 0.05
48 | 1800 | 67 | 55 | 32.96 | 32.14 | 0.06
48 | 1800 | 62 | 35 | 64.96 | 57.83 | 0.05
48 | 1800 | 62 | 40 | 54.92 | 52.3 | 0.05
48 | 1800 | 62 | 45 | 44.06 | 46.35 | 0.07
48 | 1800 | 62 | 50 | 35.97 | 35.97 | 0.17
48 | 1800 | 62 | 55 | 29.59 | 29.59 | 0.31
60 | 1600 | 72 | 35 | 118.17 | 60.42 | 0
60 | 1600 | 72 | 40 | 106.56 | 54.57 | 0
60 | 1600 | 72 | 45 | 93.41 | 48.24 | 0.02
60 | 1600 | 72 | 50 | 78.64 | 41.59 | 0.02
60 | 1600 | 72 | 55 | 62.13 | 34.63 | 0.03
60 | 1600 | 67 | 35 | 96.74 | 62.87 | 0.03
60 | 1600 | 67 | 40 | 84.83 | 56.56 | 0.03
60 | 1600 | 67 | 45 | 71.43 | 49.91 | 0.03
60 | 1600 | 67 | 50 | 56.41 | 42.93 | 0.03
60 | 1600 | 67 | 55 | 39.37 | 35.48 | 0.04
60 | 1600 | 62 | 35 | 77.24 | 64.78 | 0.03
60 | 1600 | 62 | 40 | 65.1 | 58.16 | 0.03
60 | 1600 | 62 | 45 | 51.83 | 51.23 | 0.04
60 | 1600 | 62 | 50 | 41 | 41 | 0.12
60 | 1600 | 62 | 55 | 33.67 | 33.67 | 0.27
60 | 1750 | 72 | 35 | 129.14 | 66.15 | 0
60 | 1750 | 72 | 40 | 116.46 | 59.92 | 0
60 | 1750 | 72 | 45 | 102.18 | 53.13 | 0.02
60 | 1750 | 72 | 50 | 86.08 | 45.94 | 0.03
60 | 1750 | 72 | 55 | 68 | 38.39 | 0.03
60 | 1750 | 67 | 35 | 105.94 | 69.36 | 0.04
60 | 1750 | 67 | 40 | 92.95 | 62.59 | 0.04
60 | 1750 | 67 | 45 | 78.33 | 55.41 | 0.04
60 | 1750 | 67 | 50 | 61.93 | 47.86 | 0.04
60 | 1750 | 67 | 55 | 43.49 | 39.82 | 0.05
60 | 1750 | 62 | 35 | 84.76 | 71.94 | 0.04
60 | 1750 | 62 | 40 | 71.53 | 64.8 | 0.04
60 | 1750 | 62 | 45 | 57.37 | 57.38 | 0.05
60 | 1750 | 62 | 50 | 45.94 | 45.94 | 0.14
60 | 1750 | 62 | 55 | 37.65 | 37.65 | 0.29
60 | 2000 | 72 | 35 | 139.03 | 71.41 | 0
60 | 2000 | 72 | 40 | 125.46 | 64.82 | 0.01
60 | 2000 | 72 | 45 | 110.15 | 57.64 | 0.03
60 | 2000 | 72 | 50 | 92.83 | 49.99 | 0.04
60 | 2000 | 72 | 55 | 73.33 | 41.92 | 0.04
60 | 2000 | 67 | 35 | 114.27 | 75.38 | 0.05
60 | 2000 | 67 | 40 | 100.34 | 68.21 | 0.05
60 | 2000 | 67 | 45 | 84.61 | 60.58 | 0.05
60 | 2000 | 67 | 50 | 66.92 | 52.51 | 0.05
60 | 2000 | 67 | 55 | 47.25 | 43.94 | 0.06
60 | 2000 | 62 | 35 | 91.59 | 78.67 | 0.05
60 | 2000 | 62 | 40 | 77.41 | 71.08 | 0.05
60 | 2000 | 62 | 45 | 62.32 | 63.11 | 0.07
60 | 2000 | 62 | 50 | 50.6 | 50.6 | 0.16
60 | 2000 | 62 | 55 | 41.54 | 41.54 | 0.31

## GA5_Condenser_Only
Model | Size_Nom | SST_F | ODB_F | TCG_kBtu | SDT_F | kW_ODU | Source: GA5SAN5 Product Data — Condenser Only Ratings. TCG=Gross Cooling kBtu, SDT=Sat Discharge Temp F, kW=ODU only.
GA5SAN51800W | 18 | 30 | 55 | 15.24 | 65.09 | 0.79
GA5SAN51800W | 18 | 30 | 65 | 14.16 | 74.55 | 0.9
GA5SAN51800W | 18 | 30 | 75 | 13.22 | 84.14 | 1.02
GA5SAN51800W | 18 | 30 | 85 | 12.36 | 93.79 | 1.16
GA5SAN51800W | 18 | 30 | 95 | 11.54 | 103.41 | 1.3
GA5SAN51800W | 18 | 30 | 105 | 10.71 | 112.99 | 1.47
GA5SAN51800W | 18 | 30 | 115 | 9.86 | 122.5 | 1.66
GA5SAN51800W | 18 | 35 | 55 | 16.74 | 65.74 | 0.77
GA5SAN51800W | 18 | 35 | 65 | 15.61 | 75.28 | 0.89
GA5SAN51800W | 18 | 35 | 75 | 14.63 | 84.85 | 1.02
GA5SAN51800W | 18 | 35 | 85 | 13.74 | 94.4 | 1.15
GA5SAN51800W | 18 | 35 | 95 | 12.86 | 104.06 | 1.3
GA5SAN51800W | 18 | 35 | 105 | 11.98 | 113.6 | 1.47
GA5SAN51800W | 18 | 35 | 115 | 11.05 | 123.07 | 1.66
GA5SAN51800W | 18 | 40 | 55 | 18.29 | 66.55 | 0.76
GA5SAN51800W | 18 | 40 | 65 | 17.17 | 76 | 0.88
GA5SAN51800W | 18 | 40 | 75 | 16.15 | 85.55 | 1.01
GA5SAN51800W | 18 | 40 | 85 | 15.21 | 95.1 | 1.14
GA5SAN51800W | 18 | 40 | 95 | 14.28 | 104.75 | 1.3
GA5SAN51800W | 18 | 40 | 105 | 13.34 | 114.24 | 1.47
GA5SAN51800W | 18 | 40 | 115 | 12.35 | 123.7 | 1.66
GA5SAN51800W | 18 | 45 | 55 | 19.96 | 67.31 | 0.74
GA5SAN51800W | 18 | 45 | 65 | 18.8 | 76.78 | 0.87
GA5SAN51800W | 18 | 45 | 75 | 17.76 | 86.33 | 1
GA5SAN51800W | 18 | 45 | 85 | 16.78 | 95.86 | 1.13
GA5SAN51800W | 18 | 45 | 95 | 15.82 | 105.34 | 1.29
GA5SAN51800W | 18 | 45 | 105 | 14.81 | 114.95 | 1.46
GA5SAN51800W | 18 | 45 | 115 | 13.75 | 124.22 | 1.65
GA5SAN51800W | 18 | 50 | 55 | 21.71 | 68.22 | 0.7
GA5SAN51800W | 18 | 50 | 65 | 20.54 | 77.64 | 0.85
GA5SAN51800W | 18 | 50 | 75 | 19.48 | 87.12 | 0.98
GA5SAN51800W | 18 | 50 | 85 | 18.46 | 96.65 | 1.12
GA5SAN51800W | 18 | 50 | 95 | 17.45 | 106.1 | 1.28
GA5SAN51800W | 18 | 50 | 105 | 16.37 | 115.72 | 1.46
GA5SAN51800W | 18 | 50 | 115 | 15.25 | 124.97 | 1.65
GA5SAN51800W | 18 | 55 | 55 | 23.58 | 69 | 0.71
GA5SAN51800W | 18 | 55 | 65 | 22.4 | 78.42 | 0.83
GA5SAN51800W | 18 | 55 | 75 | 21.3 | 87.98 | 0.97
GA5SAN51800W | 18 | 55 | 85 | 20.24 | 97.51 | 1.11
GA5SAN51800W | 18 | 55 | 95 | 19.18 | 106.98 | 1.27
GA5SAN51800W | 18 | 55 | 105 | 18.05 | 116.5 | 1.45
GA5SAN51800W | 18 | 55 | 115 | 16.87 | 125.72 | 1.65
GA5SAN52400W | 24 | 30 | 55 | 20 | 65.31 | 1.02
GA5SAN52400W | 24 | 30 | 65 | 18.97 | 74.85 | 1.14
GA5SAN52400W | 24 | 30 | 75 | 17.99 | 84.45 | 1.29
GA5SAN52400W | 24 | 30 | 85 | 16.99 | 94.06 | 1.45
GA5SAN52400W | 24 | 30 | 95 | 15.99 | 103.6 | 1.64
GA5SAN52400W | 24 | 30 | 105 | 14.91 | 113.23 | 1.86
GA5SAN52400W | 24 | 30 | 115 | 13.8 | 122.83 | 2.11
GA5SAN52400W | 24 | 35 | 55 | 22.12 | 66.11 | 1.01
GA5SAN52400W | 24 | 35 | 65 | 21.01 | 75.65 | 1.14
GA5SAN52400W | 24 | 35 | 75 | 19.93 | 85.18 | 1.28
GA5SAN52400W | 24 | 35 | 85 | 18.85 | 94.74 | 1.45
GA5SAN52400W | 24 | 35 | 95 | 17.73 | 104.34 | 1.64
GA5SAN52400W | 24 | 35 | 105 | 16.58 | 113.87 | 1.85
GA5SAN52400W | 24 | 35 | 115 | 15.42 | 123.24 | 2.1
GA5SAN52400W | 24 | 40 | 55 | 24.39 | 66.98 | 1
GA5SAN52400W | 24 | 40 | 65 | 23.2 | 76.46 | 1.13
GA5SAN52400W | 24 | 40 | 75 | 22.02 | 85.94 | 1.27
GA5SAN52400W | 24 | 40 | 85 | 20.84 | 95.47 | 1.44
GA5SAN52400W | 24 | 40 | 95 | 19.63 | 105.03 | 1.63
GA5SAN52400W | 24 | 40 | 105 | 18.38 | 114.55 | 1.85
GA5SAN52400W | 24 | 40 | 115 | 17.1 | 123.89 | 2.09
GA5SAN52400W | 24 | 45 | 55 | 26.81 | 67.95 | 0.99
GA5SAN52400W | 24 | 45 | 65 | 25.52 | 77.35 | 1.12
GA5SAN52400W | 24 | 45 | 75 | 24.25 | 86.78 | 1.27
GA5SAN52400W | 24 | 45 | 85 | 22.98 | 96.2 | 1.43
GA5SAN52400W | 24 | 45 | 95 | 21.66 | 105.73 | 1.62
GA5SAN52400W | 24 | 45 | 105 | 20.3 | 115.26 | 1.84
GA5SAN52400W | 24 | 45 | 115 | 18.82 | 124.22 | 2.08
GA5SAN52400W | 24 | 50 | 55 | 29.4 | 68.92 | 0.98
GA5SAN52400W | 24 | 50 | 65 | 28.01 | 78.23 | 1.11
GA5SAN52400W | 24 | 50 | 75 | 26.62 | 87.67 | 1.26
GA5SAN52400W | 24 | 50 | 85 | 25.24 | 97.1 | 1.42
GA5SAN52400W | 24 | 50 | 95 | 23.82 | 106.54 | 1.61
GA5SAN52400W | 24 | 50 | 105 | 22.35 | 116.01 | 1.83
GA5SAN52400W | 24 | 50 | 115 | 20.77 | 124.83 | 2.07
GA5SAN52400W | 24 | 55 | 55 | 32.14 | 70.02 | 0.97
GA5SAN52400W | 24 | 55 | 65 | 30.64 | 79.31 | 1.1
GA5SAN52400W | 24 | 55 | 75 | 29.16 | 88.59 | 1.24
GA5SAN52400W | 24 | 55 | 85 | 27.64 | 98.02 | 1.41
GA5SAN52400W | 24 | 55 | 95 | 26.1 | 107.44 | 1.79
GA5SAN52400W | 24 | 55 | 105 | 24.55 | 116.76 | 1.83
GA5SAN52400W | 24 | 55 | 115 | 22.86 | 125.64 | 2.06
GA5SAN53000W | 30 | 30 | 55 | 25.3 | 67.82 | 1.27
GA5SAN53000W | 30 | 30 | 65 | 23.61 | 77.25 | 1.48
GA5SAN53000W | 30 | 30 | 75 | 22.14 | 86.76 | 1.69
GA5SAN53000W | 30 | 30 | 85 | 20.81 | 96.32 | 1.92
GA5SAN53000W | 30 | 30 | 95 | 19.59 | 105.85 | 2.15
GA5SAN53000W | 30 | 30 | 105 | 18.39 | 115.4 | 2.41
GA5SAN53000W | 30 | 30 | 115 | 17.17 | 124.95 | 2.7
GA5SAN53000W | 30 | 35 | 55 | 27.73 | 68.77 | 1.28
GA5SAN53000W | 30 | 35 | 65 | 26 | 78.15 | 1.48
GA5SAN53000W | 30 | 35 | 75 | 24.46 | 87.63 | 1.69
GA5SAN53000W | 30 | 35 | 85 | 23.07 | 97.12 | 1.91
GA5SAN53000W | 30 | 35 | 95 | 21.73 | 106.67 | 2.15
GA5SAN53000W | 30 | 35 | 105 | 20.41 | 116.19 | 2.42
GA5SAN53000W | 30 | 35 | 115 | 19.05 | 125.65 | 2.71
GA5SAN53000W | 30 | 40 | 55 | 30.33 | 69.82 | 1.29
GA5SAN53000W | 30 | 40 | 65 | 28.57 | 79.16 | 1.48
GA5SAN53000W | 30 | 40 | 75 | 26.97 | 88.59 | 1.69
GA5SAN53000W | 30 | 40 | 85 | 25.49 | 98.04 | 1.91
GA5SAN53000W | 30 | 40 | 95 | 24.03 | 107.57 | 2.15
GA5SAN53000W | 30 | 40 | 105 | 22.59 | 117.02 | 2.42
GA5SAN53000W | 30 | 40 | 115 | 21.1 | 126.41 | 2.71
GA5SAN53000W | 30 | 45 | 55 | 33.17 | 70.82 | 1.3
GA5SAN53000W | 30 | 45 | 65 | 31.35 | 80.18 | 1.49
GA5SAN53000W | 30 | 45 | 75 | 29.67 | 89.63 | 1.69
GA5SAN53000W | 30 | 45 | 85 | 28.08 | 99.06 | 1.91
GA5SAN53000W | 30 | 45 | 95 | 26.53 | 108.5 | 2.15
GA5SAN53000W | 30 | 45 | 105 | 24.94 | 117.91 | 2.41
GA5SAN53000W | 30 | 45 | 115 | 23.31 | 127.15 | 2.71
GA5SAN53000W | 30 | 50 | 55 | 36.19 | 71.95 | 1.32
GA5SAN53000W | 30 | 50 | 65 | 34.31 | 81.32 | 1.49
GA5SAN53000W | 30 | 50 | 75 | 32.57 | 90.7 | 1.69
GA5SAN53000W | 30 | 50 | 85 | 30.89 | 100.04 | 1.9
GA5SAN53000W | 30 | 50 | 95 | 29.21 | 109.46 | 2.14
GA5SAN53000W | 30 | 50 | 105 | 27.47 | 118.85 | 2.41
GA5SAN53000W | 30 | 50 | 115 | 25.65 | 128.18 | 2.71
GA5SAN53000W | 30 | 55 | 55 | 39.43 | 73.16 | 1.33
GA5SAN53000W | 30 | 55 | 65 | 37.51 | 82.46 | 1.5
GA5SAN53000W | 30 | 55 | 75 | 35.67 | 91.79 | 1.69
GA5SAN53000W | 30 | 55 | 85 | 33.88 | 101.17 | 1.89
GA5SAN53000W | 30 | 55 | 95 | 32.07 | 110.51 | 2.13
GA5SAN53000W | 30 | 55 | 105 | 30.18 | 119.84 | 2.39
GA5SAN53000W | 30 | 55 | 115 | 28.19 | 129.06 | 2.69
GA5SAN53602W | 36 | 30 | 55 | 27.39 | 67.52 | 1.14
GA5SAN53602W | 36 | 30 | 65 | 26.47 | 77.36 | 1.54
GA5SAN53602W | 36 | 30 | 75 | 25.31 | 86.99 | 1.85
GA5SAN53602W | 36 | 30 | 85 | 23.95 | 96.56 | 2.13
GA5SAN53602W | 36 | 30 | 95 | 22.47 | 106.05 | 2.4
GA5SAN53602W | 36 | 30 | 105 | 20.92 | 115.49 | 2.68
GA5SAN53602W | 36 | 30 | 115 | 19.32 | 124.98 | 3
GA5SAN53602W | 36 | 35 | 55 | 30.34 | 68.52 | 1.15
GA5SAN53602W | 36 | 35 | 65 | 29.3 | 78.24 | 1.54
GA5SAN53602W | 36 | 35 | 75 | 27.97 | 87.91 | 1.86
GA5SAN53602W | 36 | 35 | 85 | 26.46 | 97.42 | 2.14
GA5SAN53602W | 36 | 35 | 95 | 24.84 | 106.87 | 2.41
GA5SAN53602W | 36 | 35 | 105 | 23.15 | 116.25 | 2.69
GA5SAN53602W | 36 | 35 | 115 | 21.4 | 125.69 | 3.02
GA5SAN53602W | 36 | 40 | 55 | 33.54 | 69.58 | 1.16
GA5SAN53602W | 36 | 40 | 65 | 32.31 | 79.28 | 1.54
GA5SAN53602W | 36 | 40 | 75 | 30.85 | 88.79 | 1.85
GA5SAN53602W | 36 | 40 | 85 | 29.18 | 98.28 | 2.13
GA5SAN53602W | 36 | 40 | 95 | 27.38 | 107.7 | 2.41
GA5SAN53602W | 36 | 40 | 105 | 25.53 | 117.09 | 2.7
GA5SAN53602W | 36 | 40 | 115 | 23.64 | 126.41 | 3.04
GA5SAN53602W | 36 | 45 | 55 | 36.96 | 70.68 | 1.16
GA5SAN53602W | 36 | 45 | 65 | 35.55 | 80.32 | 1.53
GA5SAN53602W | 36 | 45 | 75 | 33.89 | 89.86 | 1.84
GA5SAN53602W | 36 | 45 | 85 | 32.05 | 99.28 | 2.12
GA5SAN53602W | 36 | 45 | 95 | 30.11 | 108.58 | 2.4
GA5SAN53602W | 36 | 45 | 105 | 28.07 | 117.94 | 2.7
GA5SAN53602W | 36 | 45 | 115 | 25.99 | 127.27 | 3.05
GA5SAN53602W | 36 | 50 | 55 | 40.63 | 71.92 | 1.16
GA5SAN53602W | 36 | 50 | 65 | 39.02 | 81.51 | 1.52
GA5SAN53602W | 36 | 50 | 75 | 37.16 | 90.93 | 1.83
GA5SAN53602W | 36 | 50 | 85 | 35.13 | 100.14 | 2.11
GA5SAN53602W | 36 | 50 | 95 | 32.98 | 109.58 | 2.39
GA5SAN53602W | 36 | 50 | 105 | 30.76 | 118.8 | 2.69
GA5SAN53602W | 36 | 50 | 115 | 28.51 | 128.08 | 3.05
GA5SAN53602W | 36 | 55 | 55 | 44.54 | 73.21 | 1.16
GA5SAN53602W | 36 | 55 | 65 | 42.71 | 82.66 | 1.51
GA5SAN53602W | 36 | 55 | 75 | 40.64 | 92.08 | 1.81
GA5SAN53602W | 36 | 55 | 85 | 38.42 | 101.33 | 2.08
GA5SAN53602W | 36 | 55 | 95 | 36.06 | 110.57 | 2.36
GA5SAN53602W | 36 | 55 | 105 | 33.63 | 119.73 | 2.67
GA5SAN53602W | 36 | 55 | 115 | 31.16 | 128.98 | 3.04
GA5SAN54201W | 42 | 30 | 55 | 34.51 | 66.49 | 1.79
GA5SAN54201W | 42 | 30 | 65 | 32.93 | 76.08 | 2.01
GA5SAN54201W | 42 | 30 | 75 | 31.32 | 85.66 | 2.26
GA5SAN54201W | 42 | 30 | 85 | 29.69 | 95.24 | 2.54
GA5SAN54201W | 42 | 30 | 95 | 27.98 | 104.78 | 2.87
GA5SAN54201W | 42 | 30 | 105 | 26.16 | 114.3 | 3.25
GA5SAN54201W | 42 | 30 | 115 | 24.24 | 123.79 | 3.69
GA5SAN54201W | 42 | 35 | 55 | 38.13 | 67.53 | 1.79
GA5SAN54201W | 42 | 35 | 65 | 36.36 | 77.03 | 2.01
GA5SAN54201W | 42 | 35 | 75 | 34.6 | 86.56 | 2.26
GA5SAN54201W | 42 | 35 | 85 | 32.82 | 96.09 | 2.54
GA5SAN54201W | 42 | 35 | 95 | 30.98 | 105.62 | 2.87
GA5SAN54201W | 42 | 35 | 105 | 29.02 | 115.09 | 3.25
GA5SAN54201W | 42 | 35 | 115 | 26.94 | 124.53 | 3.69
GA5SAN54201W | 42 | 40 | 55 | 41.99 | 68.61 | 1.79
GA5SAN54201W | 42 | 40 | 65 | 40.07 | 78.07 | 2.01
GA5SAN54201W | 42 | 40 | 75 | 38.16 | 87.55 | 2.26
GA5SAN54201W | 42 | 40 | 85 | 36.21 | 97.04 | 2.55
GA5SAN54201W | 42 | 40 | 95 | 34.21 | 106.52 | 2.88
GA5SAN54201W | 42 | 40 | 105 | 32.09 | 115.95 | 3.26
GA5SAN54201W | 42 | 40 | 115 | 29.83 | 125.33 | 3.69
GA5SAN54201W | 42 | 45 | 55 | 46.17 | 69.8 | 1.79
GA5SAN54201W | 42 | 45 | 65 | 44.07 | 79.19 | 2.01
GA5SAN54201W | 42 | 45 | 75 | 41.98 | 88.62 | 2.26
GA5SAN54201W | 42 | 45 | 85 | 39.86 | 98.06 | 2.55
GA5SAN54201W | 42 | 45 | 95 | 37.66 | 107.47 | 2.88
GA5SAN54201W | 42 | 45 | 105 | 35.36 | 116.86 | 3.26
GA5SAN54201W | 42 | 45 | 115 | 32.9 | 126.18 | 3.7
GA5SAN54201W | 42 | 50 | 55 | 50.68 | 71.09 | 1.78
GA5SAN54201W | 42 | 50 | 65 | 48.38 | 80.41 | 2.01
GA5SAN54201W | 42 | 50 | 75 | 46.09 | 89.77 | 2.27
GA5SAN54201W | 42 | 50 | 85 | 43.78 | 99.17 | 2.56
GA5SAN54201W | 42 | 50 | 95 | 41.35 | 108.5 | 2.89
GA5SAN54201W | 42 | 50 | 105 | 38.84 | 117.82 | 3.27
GA5SAN54201W | 42 | 50 | 115 | 36.17 | 127.1 | 3.71
GA5SAN54201W | 42 | 55 | 55 | 55.51 | 72.47 | 1.78
GA5SAN54201W | 42 | 55 | 65 | 53 | 81.73 | 2.01
GA5SAN54201W | 42 | 55 | 75 | 50.49 | 91.02 | 2.27
GA5SAN54201W | 42 | 55 | 85 | 47.94 | 100.26 | 2.57
GA5SAN54201W | 42 | 55 | 95 | 45.32 | 109.61 | 2.9
GA5SAN54201W | 42 | 55 | 105 | 41.62 | 118.54 | 3.27
GA5SAN54201W | 42 | 55 | 115 | 39.66 | 128.07 | 3.72
GA5SAN54801W | 48 | 30 | 55 | 40.62 | 71.79 | 2.19
GA5SAN54801W | 48 | 30 | 65 | 38.68 | 81.15 | 2.42
GA5SAN54801W | 48 | 30 | 75 | 36.79 | 90.56 | 2.7
GA5SAN54801W | 48 | 30 | 85 | 34.81 | 99.93 | 3.03
GA5SAN54801W | 48 | 30 | 95 | 32.7 | 109.24 | 3.42
GA5SAN54801W | 48 | 30 | 105 | 30.37 | 118.49 | 3.89
GA5SAN54801W | 48 | 30 | 115 | 27.82 | 127.62 | 4.43
GA5SAN54801W | 48 | 35 | 55 | 44.68 | 73.27 | 2.2
GA5SAN54801W | 48 | 35 | 65 | 42.64 | 82.61 | 2.43
GA5SAN54801W | 48 | 35 | 75 | 40.58 | 91.93 | 2.72
GA5SAN54801W | 48 | 35 | 85 | 38.46 | 101.25 | 3.05
GA5SAN54801W | 48 | 35 | 95 | 36.16 | 110.5 | 3.45
GA5SAN54801W | 48 | 35 | 105 | 33.66 | 119.68 | 3.91
GA5SAN54801W | 48 | 35 | 115 | 30.91 | 128.76 | 4.45
GA5SAN54801W | 48 | 40 | 55 | 49.05 | 74.86 | 2.19
GA5SAN54801W | 48 | 40 | 65 | 46.87 | 84.14 | 2.44
GA5SAN54801W | 48 | 40 | 75 | 44.64 | 93.4 | 2.73
GA5SAN54801W | 48 | 40 | 85 | 42.34 | 102.67 | 3.08
GA5SAN54801W | 48 | 40 | 95 | 39.86 | 111.87 | 3.48
GA5SAN54801W | 48 | 40 | 105 | 37.13 | 120.97 | 3.94
GA5SAN54801W | 48 | 40 | 115 | 34.16 | 129.97 | 4.47
GA5SAN54801W | 48 | 45 | 55 | 53.76 | 76.58 | 2.19
GA5SAN54801W | 48 | 45 | 65 | 51.4 | 85.79 | 2.45
GA5SAN54801W | 48 | 45 | 75 | 49 | 95.03 | 2.75
GA5SAN54801W | 48 | 45 | 85 | 46.47 | 104.18 | 3.1
GA5SAN54801W | 48 | 45 | 95 | 43.76 | 113.29 | 3.51
GA5SAN54801W | 48 | 45 | 105 | 40.8 | 122.31 | 3.97
GA5SAN54801W | 48 | 45 | 115 | 37.58 | 131.23 | 4.5
GA5SAN54801W | 48 | 50 | 55 | 58.82 | 78.47 | 2.19
GA5SAN54801W | 48 | 50 | 65 | 56.27 | 87.62 | 2.46
GA5SAN54801W | 48 | 50 | 75 | 53.62 | 96.7 | 2.77
GA5SAN54801W | 48 | 50 | 85 | 50.86 | 105.8 | 3.14
GA5SAN54801W | 48 | 50 | 95 | 47.89 | 114.81 | 3.55
GA5SAN54801W | 48 | 50 | 105 | 44.68 | 123.73 | 4.02
GA5SAN54801W | 48 | 50 | 115 | 41.17 | 132.56 | 4.55
GA5SAN54801W | 48 | 55 | 55 | 64.19 | 80.42 | 2.18
GA5SAN54801W | 48 | 55 | 65 | 61.41 | 89.48 | 2.47
GA5SAN54801W | 48 | 55 | 75 | 58.53 | 98.52 | 2.8
GA5SAN54801W | 48 | 55 | 85 | 55.5 | 107.52 | 3.17
GA5SAN54801W | 48 | 55 | 95 | 52.25 | 116.44 | 3.59
GA5SAN54801W | 48 | 55 | 105 | 48.74 | 125.26 | 4.07
GA5SAN54801W | 48 | 55 | 115 | 44.94 | 133.98 | 4.6
GA5SAN56000W | 60 | 30 | 55 | 48.39 | 71.12 | 2.67
GA5SAN56000W | 60 | 30 | 65 | 46.46 | 80.58 | 2.98
GA5SAN56000W | 60 | 30 | 75 | 44.41 | 90.03 | 3.33
GA5SAN56000W | 60 | 30 | 85 | 42.14 | 99.42 | 3.75
GA5SAN56000W | 60 | 30 | 95 | 39.61 | 108.76 | 4.24
GA5SAN56000W | 60 | 30 | 105 | 36.87 | 118.03 | 4.81
GA5SAN56000W | 60 | 30 | 115 | 33.84 | 127.21 | 5.47
GA5SAN56000W | 60 | 35 | 55 | 53.57 | 72.66 | 2.67
GA5SAN56000W | 60 | 35 | 65 | 51.42 | 82.04 | 2.99
GA5SAN56000W | 60 | 35 | 75 | 49.13 | 91.4 | 3.35
GA5SAN56000W | 60 | 35 | 85 | 46.67 | 100.74 | 3.78
GA5SAN56000W | 60 | 35 | 95 | 43.97 | 110.03 | 4.27
GA5SAN56000W | 60 | 35 | 105 | 40.91 | 119.24 | 4.83
GA5SAN56000W | 60 | 35 | 115 | 37.84 | 128.38 | 5.49
GA5SAN56000W | 60 | 40 | 55 | 59.08 | 74.29 | 2.68
GA5SAN56000W | 60 | 40 | 65 | 56.66 | 83.58 | 3.01
GA5SAN56000W | 60 | 40 | 75 | 54.16 | 92.9 | 3.38
GA5SAN56000W | 60 | 40 | 85 | 51.46 | 102.16 | 3.81
GA5SAN56000W | 60 | 40 | 95 | 48.53 | 111.41 | 4.3
GA5SAN56000W | 60 | 40 | 105 | 45.25 | 120.49 | 4.86
GA5SAN56000W | 60 | 40 | 115 | 42.05 | 129.64 | 5.52
GA5SAN56000W | 60 | 45 | 55 | 64.91 | 76.02 | 2.69
GA5SAN56000W | 60 | 45 | 65 | 62.23 | 85.23 | 3.03
GA5SAN56000W | 60 | 45 | 75 | 59.44 | 94.44 | 3.41
GA5SAN56000W | 60 | 45 | 85 | 56.52 | 103.64 | 3.84
GA5SAN56000W | 60 | 45 | 95 | 53.39 | 112.79 | 4.34
GA5SAN56000W | 60 | 45 | 105 | 50.05 | 121.87 | 4.92
GA5SAN56000W | 60 | 45 | 115 | 46.42 | 130.94 | 5.57
GA5SAN56000W | 60 | 50 | 55 | 71.04 | 77.84 | 2.71
GA5SAN56000W | 60 | 50 | 65 | 68.07 | 86.96 | 3.06
GA5SAN56000W | 60 | 50 | 75 | 65.01 | 96.08 | 3.45
GA5SAN56000W | 60 | 50 | 85 | 61.78 | 105.18 | 3.89
GA5SAN56000W | 60 | 50 | 95 | 58.44 | 114.28 | 4.4
GA5SAN56000W | 60 | 50 | 105 | 54.85 | 123.31 | 4.97
GA5SAN56000W | 60 | 50 | 115 | 51.01 | 132.27 | 5.63
GA5SAN56000W | 60 | 55 | 55 | 77.48 | 79.79 | 2.75
GA5SAN56000W | 60 | 55 | 65 | 74.17 | 88.86 | 3.1
GA5SAN56000W | 60 | 55 | 75 | 70.81 | 97.81 | 3.5
GA5SAN56000W | 60 | 55 | 85 | 67.33 | 106.85 | 3.95
GA5SAN56000W | 60 | 55 | 95 | 63.68 | 115.85 | 4.46
GA5SAN56000W | 60 | 55 | 105 | 59.82 | 124.79 | 5.04
GA5SAN56000W | 60 | 55 | 115 | 55.73 | 133.68 | 5.7

## GA8_Condenser_Only
Model | Size_Nom | Stage | SST_F | ODB_F | TCG_kBtu | SDT_F | kW_ODU | Source: GA8TAN5 Product Data — Condenser Only Ratings (High Stage and Low Stage).
GA8TAN52400W | 24 | High | 30 | 55 | 19.99 | 67.6 | 0.92
GA8TAN52400W | 24 | High | 30 | 65 | 19.13 | 77.31 | 1.06
GA8TAN52400W | 24 | High | 30 | 75 | 18.21 | 86.93 | 1.21
GA8TAN52400W | 24 | High | 30 | 85 | 17.23 | 96.55 | 1.37
GA8TAN52400W | 24 | High | 30 | 95 | 16.24 | 105.96 | 1.55
GA8TAN52400W | 24 | High | 30 | 105 | 15.15 | 115.63 | 1.76
GA8TAN52400W | 24 | High | 30 | 115 | 14.05 | 125.05 | 2
GA8TAN52400W | 24 | High | 35 | 55 | 22.03 | 68.61 | 0.91
GA8TAN52400W | 24 | High | 35 | 65 | 21.12 | 78.21 | 1.06
GA8TAN52400W | 24 | High | 35 | 75 | 20.13 | 87.84 | 1.21
GA8TAN52400W | 24 | High | 35 | 85 | 19.07 | 97.46 | 1.38
GA8TAN52400W | 24 | High | 35 | 95 | 17.99 | 106.85 | 1.56
GA8TAN52400W | 24 | High | 35 | 105 | 16.83 | 116.4 | 1.77
GA8TAN52400W | 24 | High | 35 | 115 | 15.55 | 125.46 | 2
GA8TAN52400W | 24 | High | 40 | 55 | 24.23 | 69.57 | 0.9
GA8TAN52400W | 24 | High | 40 | 65 | 23.25 | 79.2 | 1.05
GA8TAN52400W | 24 | High | 40 | 75 | 22.19 | 88.83 | 1.21
GA8TAN52400W | 24 | High | 40 | 85 | 21.05 | 98.4 | 1.38
GA8TAN52400W | 24 | High | 40 | 95 | 19.86 | 107.85 | 1.57
GA8TAN52400W | 24 | High | 40 | 105 | 18.62 | 117.25 | 1.78
GA8TAN52400W | 24 | High | 40 | 115 | 17.24 | 126.31 | 2.01
GA8TAN52400W | 24 | High | 45 | 55 | 26.58 | 70.65 | 0.88
GA8TAN52400W | 24 | High | 45 | 65 | 25.54 | 80.25 | 1.04
GA8TAN52400W | 24 | High | 45 | 75 | 24.39 | 89.86 | 1.21
GA8TAN52400W | 24 | High | 45 | 85 | 23.18 | 99.35 | 1.38
GA8TAN52400W | 24 | High | 45 | 95 | 21.88 | 108.83 | 1.58
GA8TAN52400W | 24 | High | 45 | 105 | 20.53 | 118.2 | 1.79
GA8TAN52400W | 24 | High | 45 | 115 | 19.07 | 127.05 | 2.02
GA8TAN52400W | 24 | High | 50 | 55 | 29.09 | 71.81 | 0.86
GA8TAN52400W | 24 | High | 50 | 65 | 27.98 | 81.41 | 1.03
GA8TAN52400W | 24 | High | 50 | 75 | 26.77 | 90.82 | 1.2
GA8TAN52400W | 24 | High | 50 | 85 | 25.44 | 100.4 | 1.39
GA8TAN52400W | 24 | High | 50 | 95 | 24.06 | 109.78 | 1.58
GA8TAN52400W | 24 | High | 50 | 105 | 22.59 | 119.15 | 1.8
GA8TAN52400W | 24 | High | 50 | 115 | 21.04 | 128.09 | 2.04
GA8TAN52400W | 24 | High | 55 | 55 | 31.78 | 73 | 0.84
GA8TAN52400W | 24 | High | 55 | 65 | 30.59 | 82.57 | 1.02
GA8TAN52400W | 24 | High | 55 | 75 | 29.27 | 92.08 | 1.2
GA8TAN52400W | 24 | High | 55 | 85 | 27.86 | 101.52 | 1.39
GA8TAN52400W | 24 | High | 55 | 95 | 26.37 | 110.87 | 1.59
GA8TAN52400W | 24 | High | 55 | 105 | 24.79 | 120.15 | 1.81
GA8TAN52400W | 24 | High | 55 | 115 | 23.15 | 129.25 | 2.06
GA8TAN52400W | 24 | Low | 30 | 55 | 13.05 | 64.12 | 0.65
GA8TAN52400W | 24 | Low | 30 | 65 | 12.75 | 73.97 | 0.76
GA8TAN52400W | 24 | Low | 30 | 75 | 12.34 | 83.74 | 0.86
GA8TAN52400W | 24 | Low | 30 | 85 | 11.79 | 93.49 | 0.97
GA8TAN52400W | 24 | Low | 30 | 95 | 11.1 | 103.12 | 1.08
GA8TAN52400W | 24 | Low | 30 | 105 | 10.26 | 112.67 | 1.2
GA8TAN52400W | 24 | Low | 30 | 115 | 9.27 | 122.09 | 1.33
GA8TAN52400W | 24 | Low | 35 | 55 | 14.6 | 64.86 | 0.63
GA8TAN52400W | 24 | Low | 35 | 65 | 14.22 | 74.64 | 0.73
GA8TAN52400W | 24 | Low | 35 | 75 | 13.75 | 84.42 | 0.84
GA8TAN52400W | 24 | Low | 35 | 85 | 13.16 | 94.08 | 0.95
GA8TAN52400W | 24 | Low | 35 | 95 | 12.36 | 103.28 | 1.06
GA8TAN52400W | 24 | Low | 35 | 105 | 11.57 | 113.28 | 1.19
GA8TAN52400W | 24 | Low | 35 | 115 | 10.59 | 122.62 | 1.31
GA8TAN52400W | 24 | Low | 40 | 55 | 16.27 | 65.61 | 0.6
GA8TAN52400W | 24 | Low | 40 | 65 | 15.8 | 75.4 | 0.71
GA8TAN52400W | 24 | Low | 40 | 75 | 15.26 | 85.12 | 0.82
GA8TAN52400W | 24 | Low | 40 | 85 | 14.62 | 94.79 | 0.93
GA8TAN52400W | 24 | Low | 40 | 95 | 13.85 | 104.19 | 1.04
GA8TAN52400W | 24 | Low | 40 | 105 | 12.98 | 113.88 | 1.17
GA8TAN52400W | 24 | Low | 40 | 115 | 11.95 | 123.25 | 1.3
GA8TAN52400W | 24 | Low | 45 | 55 | 18.07 | 66.46 | 0.57
GA8TAN52400W | 24 | Low | 45 | 65 | 17.51 | 76.18 | 0.68
GA8TAN52400W | 24 | Low | 45 | 75 | 16.88 | 85.93 | 0.8
GA8TAN52400W | 24 | Low | 45 | 85 | 16.19 | 95.51 | 0.91
GA8TAN52400W | 24 | Low | 45 | 95 | 15.39 | 105.05 | 1.03
GA8TAN52400W | 24 | Low | 45 | 105 | 14.44 | 114.63 | 1.16
GA8TAN52400W | 24 | Low | 45 | 115 | 13.4 | 123.93 | 1.28
GA8TAN52400W | 24 | Low | 50 | 55 | 19.99 | 67.37 | 0.53
GA8TAN52400W | 24 | Low | 50 | 65 | 19.34 | 77.02 | 0.66
GA8TAN52400W | 24 | Low | 50 | 75 | 18.64 | 86.65 | 0.77
GA8TAN52400W | 24 | Low | 50 | 85 | 17.86 | 96.27 | 0.89
GA8TAN52400W | 24 | Low | 50 | 95 | 17 | 105.8 | 1.01
GA8TAN52400W | 24 | Low | 50 | 105 | 16.04 | 115.27 | 1.14
GA8TAN52400W | 24 | Low | 50 | 115 | 14.88 | 124.2 | 1.26
GA8TAN52400W | 24 | Low | 55 | 55 | 22.05 | 68.38 | 0.5
GA8TAN52400W | 24 | Low | 55 | 65 | 21.3 | 77.91 | 0.63
GA8TAN52400W | 24 | Low | 55 | 75 | 20.5 | 87.5 | 0.75
GA8TAN52400W | 24 | Low | 55 | 85 | 19.67 | 97 | 0.87
GA8TAN52400W | 24 | Low | 55 | 95 | 18.74 | 106.54 | 0.99
GA8TAN52400W | 24 | Low | 55 | 105 | 17.72 | 116 | 1.12
GA8TAN52400W | 24 | Low | 55 | 115 | 16.51 | 124.83 | 1.24
GA8TAN53600W | 36 | High | 30 | 55 | 30.55 | 67.32 | 1.47
GA8TAN53600W | 36 | High | 30 | 65 | 29 | 76.75 | 1.68
GA8TAN53600W | 36 | High | 30 | 75 | 27.56 | 86.28 | 1.9
GA8TAN53600W | 36 | High | 30 | 85 | 26.1 | 95.8 | 2.13
GA8TAN53600W | 36 | High | 30 | 95 | 24.58 | 105.3 | 2.39
GA8TAN53600W | 36 | High | 30 | 105 | 23 | 114.78 | 2.69
GA8TAN53600W | 36 | High | 30 | 115 | 21.34 | 124.24 | 3.05
GA8TAN53600W | 36 | High | 35 | 55 | 33.6 | 68.39 | 1.49
GA8TAN53600W | 36 | High | 35 | 65 | 31.99 | 77.83 | 1.7
GA8TAN53600W | 36 | High | 35 | 75 | 30.41 | 87.29 | 1.91
GA8TAN53600W | 36 | High | 35 | 85 | 28.8 | 96.75 | 2.14
GA8TAN53600W | 36 | High | 35 | 95 | 27.16 | 106.23 | 2.4
GA8TAN53600W | 36 | High | 35 | 105 | 25.45 | 115.65 | 2.71
GA8TAN53600W | 36 | High | 35 | 115 | 23.63 | 125.05 | 3.06
GA8TAN53600W | 36 | High | 40 | 55 | 36.93 | 69.66 | 1.52
GA8TAN53600W | 36 | High | 40 | 65 | 35.15 | 78.95 | 1.71
GA8TAN53600W | 36 | High | 40 | 75 | 33.46 | 88.37 | 1.92
GA8TAN53600W | 36 | High | 40 | 85 | 31.73 | 97.79 | 2.15
GA8TAN53600W | 36 | High | 40 | 95 | 29.96 | 107.2 | 2.41
GA8TAN53600W | 36 | High | 40 | 105 | 28.09 | 116.59 | 2.72
GA8TAN53600W | 36 | High | 40 | 115 | 26.1 | 125.92 | 3.08
GA8TAN53600W | 36 | High | 45 | 55 | 40.43 | 70.9 | 1.53
GA8TAN53600W | 36 | High | 45 | 65 | 38.61 | 80.23 | 1.73
GA8TAN53600W | 36 | High | 45 | 75 | 36.73 | 89.53 | 1.94
GA8TAN53600W | 36 | High | 45 | 85 | 34.89 | 98.93 | 2.17
GA8TAN53600W | 36 | High | 45 | 95 | 32.96 | 108.28 | 2.43
GA8TAN53600W | 36 | High | 45 | 105 | 30.88 | 117.59 | 2.73
GA8TAN53600W | 36 | High | 45 | 115 | 28.73 | 126.86 | 3.09
GA8TAN53600W | 36 | High | 50 | 55 | 44.24 | 72.31 | 1.56
GA8TAN53600W | 36 | High | 50 | 65 | 42.22 | 81.5 | 1.74
GA8TAN53600W | 36 | High | 50 | 75 | 40.27 | 90.82 | 1.95
GA8TAN53600W | 36 | High | 50 | 85 | 38.24 | 100.12 | 2.18
GA8TAN53600W | 36 | High | 50 | 95 | 36.11 | 109.39 | 2.44
GA8TAN53600W | 36 | High | 50 | 105 | 33.9 | 118.64 | 2.74
GA8TAN53600W | 36 | High | 50 | 115 | 31.53 | 127.85 | 3.1
GA8TAN53600W | 36 | High | 55 | 55 | 48.33 | 73.84 | 1.55
GA8TAN53600W | 36 | High | 55 | 65 | 46.14 | 82.93 | 1.76
GA8TAN53600W | 36 | High | 55 | 75 | 44.01 | 92.17 | 1.97
GA8TAN53600W | 36 | High | 55 | 85 | 41.82 | 101.4 | 2.19
GA8TAN53600W | 36 | High | 55 | 95 | 39.53 | 110.62 | 2.45
GA8TAN53600W | 36 | High | 55 | 105 | 37.09 | 119.77 | 2.75
GA8TAN53600W | 36 | High | 55 | 115 | 34.51 | 128.9 | 3.11
GA8TAN53600W | 36 | Low | 30 | 55 | 19.29 | 63.46 | 1.08
GA8TAN53600W | 36 | Low | 30 | 65 | 18.77 | 73.21 | 1.24
GA8TAN53600W | 36 | Low | 30 | 75 | 18.17 | 82.96 | 1.4
GA8TAN53600W | 36 | Low | 30 | 85 | 17.38 | 92.58 | 1.56
GA8TAN53600W | 36 | Low | 30 | 95 | 16.43 | 102.25 | 1.75
GA8TAN53600W | 36 | Low | 30 | 105 | 15.27 | 111.82 | 1.94
GA8TAN53600W | 36 | Low | 30 | 115 | 13.89 | 121.31 | 2.16
GA8TAN53600W | 36 | Low | 35 | 55 | 21.58 | 64.3 | 1.04
GA8TAN53600W | 36 | Low | 35 | 65 | 20.93 | 73.97 | 1.2
GA8TAN53600W | 36 | Low | 35 | 75 | 20.2 | 83.65 | 1.37
GA8TAN53600W | 36 | Low | 35 | 85 | 19.37 | 93.29 | 1.54
GA8TAN53600W | 36 | Low | 35 | 95 | 18.38 | 102.93 | 1.72
GA8TAN53600W | 36 | Low | 35 | 105 | 17.17 | 112.46 | 1.92
GA8TAN53600W | 36 | Low | 35 | 115 | 15.78 | 121.95 | 2.13
GA8TAN53600W | 36 | Low | 40 | 55 | 24.06 | 65.2 | 0.99
GA8TAN53600W | 36 | Low | 40 | 65 | 23.27 | 74.81 | 1.16
GA8TAN53600W | 36 | Low | 40 | 75 | 22.44 | 84.45 | 1.34
GA8TAN53600W | 36 | Low | 40 | 85 | 21.49 | 94.06 | 1.51
GA8TAN53600W | 36 | Low | 40 | 95 | 20.41 | 103.63 | 1.69
GA8TAN53600W | 36 | Low | 40 | 105 | 19.18 | 113.14 | 1.89
GA8TAN53600W | 36 | Low | 40 | 115 | 17.76 | 122.61 | 2.1
GA8TAN53600W | 36 | Low | 45 | 55 | 26.77 | 66.19 | 0.94
GA8TAN53600W | 36 | Low | 45 | 65 | 25.79 | 75.71 | 1.12
GA8TAN53600W | 36 | Low | 45 | 75 | 24.82 | 85.27 | 1.3
GA8TAN53600W | 36 | Low | 45 | 85 | 23.78 | 94.84 | 1.48
GA8TAN53600W | 36 | Low | 45 | 95 | 22.62 | 104.37 | 1.67
GA8TAN53600W | 36 | Low | 45 | 105 | 21.34 | 113.88 | 1.86
GA8TAN53600W | 36 | Low | 45 | 115 | 19.85 | 123.31 | 2.07
GA8TAN53600W | 36 | Low | 50 | 55 | 29.67 | 67.26 | 0.89
GA8TAN53600W | 36 | Low | 50 | 65 | 28.51 | 76.7 | 1.09
GA8TAN53600W | 36 | Low | 50 | 75 | 27.37 | 86.18 | 1.27
GA8TAN53600W | 36 | Low | 50 | 85 | 26.21 | 95.69 | 1.46
GA8TAN53600W | 36 | Low | 50 | 95 | 24.92 | 105.16 | 1.64
GA8TAN53600W | 36 | Low | 50 | 105 | 23.57 | 114.64 | 1.84
GA8TAN53600W | 36 | Low | 50 | 115 | 22.03 | 124.05 | 2.05
GA8TAN53600W | 36 | Low | 55 | 55 | 32.75 | 68.39 | 0.85
GA8TAN53600W | 36 | Low | 55 | 65 | 31.4 | 77.74 | 1.05
GA8TAN53600W | 36 | Low | 55 | 75 | 30.1 | 87.16 | 1.25
GA8TAN53600W | 36 | Low | 55 | 85 | 28.79 | 96.61 | 1.44
GA8TAN53600W | 36 | Low | 55 | 95 | 27.42 | 106.05 | 1.63
GA8TAN53600W | 36 | Low | 55 | 105 | 25.93 | 115.45 | 1.82
GA8TAN53600W | 36 | Low | 55 | 115 | 24.31 | 124.81 | 2.02
GA8TAN54800W | 48 | High | 30 | 55 | 39.86 | 68.14 | 2.06
GA8TAN54800W | 48 | High | 30 | 65 | 38.04 | 77.57 | 2.23
GA8TAN54800W | 48 | High | 30 | 75 | 36.16 | 87.04 | 2.48
GA8TAN54800W | 48 | High | 30 | 85 | 34.19 | 96.53 | 2.79
GA8TAN54800W | 48 | High | 30 | 95 | 32.14 | 106.05 | 3.17
GA8TAN54800W | 48 | High | 30 | 105 | 30.04 | 115.61 | 3.61
GA8TAN54800W | 48 | High | 30 | 115 | 27.88 | 125.16 | 4.09
GA8TAN54800W | 48 | High | 35 | 55 | 43.93 | 69.28 | 2.1
GA8TAN54800W | 48 | High | 35 | 65 | 42.04 | 78.66 | 2.26
GA8TAN54800W | 48 | High | 35 | 75 | 40.04 | 88.09 | 2.5
GA8TAN54800W | 48 | High | 35 | 85 | 37.94 | 97.53 | 2.81
GA8TAN54800W | 48 | High | 35 | 95 | 35.75 | 107.04 | 3.18
GA8TAN54800W | 48 | High | 35 | 105 | 33.47 | 116.53 | 3.61
GA8TAN54800W | 48 | High | 35 | 115 | 31.11 | 126.02 | 4.1
GA8TAN54800W | 48 | High | 40 | 55 | 48.29 | 70.52 | 2.14
GA8TAN54800W | 48 | High | 40 | 65 | 46.32 | 79.83 | 2.29
GA8TAN54800W | 48 | High | 40 | 75 | 44.21 | 89.21 | 2.52
GA8TAN54800W | 48 | High | 40 | 85 | 41.98 | 98.61 | 2.82
GA8TAN54800W | 48 | High | 40 | 95 | 39.63 | 108.1 | 3.2
GA8TAN54800W | 48 | High | 40 | 105 | 37.15 | 117.5 | 3.63
GA8TAN54800W | 48 | High | 40 | 115 | 34.57 | 126.95 | 4.12
GA8TAN54800W | 48 | High | 45 | 55 | 52.96 | 71.79 | 2.18
GA8TAN54800W | 48 | High | 45 | 65 | 50.9 | 81.08 | 2.32
GA8TAN54800W | 48 | High | 45 | 75 | 48.67 | 90.41 | 2.55
GA8TAN54800W | 48 | High | 45 | 85 | 46.3 | 99.77 | 2.85
GA8TAN54800W | 48 | High | 45 | 95 | 43.77 | 109.19 | 3.22
GA8TAN54800W | 48 | High | 45 | 105 | 41.1 | 118.57 | 3.64
GA8TAN54800W | 48 | High | 45 | 115 | 38.31 | 127.99 | 4.13
GA8TAN54800W | 48 | High | 50 | 55 | 57.97 | 73.2 | 2.15
GA8TAN54800W | 48 | High | 50 | 65 | 55.81 | 82.45 | 2.38
GA8TAN54800W | 48 | High | 50 | 75 | 53.45 | 91.74 | 2.59
GA8TAN54800W | 48 | High | 50 | 85 | 50.9 | 101 | 2.88
GA8TAN54800W | 48 | High | 50 | 95 | 48.18 | 110.39 | 3.24
GA8TAN54800W | 48 | High | 50 | 105 | 45.31 | 119.73 | 3.67
GA8TAN54800W | 48 | High | 50 | 115 | 42.29 | 129.08 | 4.15
GA8TAN54800W | 48 | High | 55 | 55 | 63.29 | 74.68 | 2.28
GA8TAN54800W | 48 | High | 55 | 65 | 61.03 | 83.9 | 2.43
GA8TAN54800W | 48 | High | 55 | 75 | 58.51 | 93.1 | 2.64
GA8TAN54800W | 48 | High | 55 | 85 | 55.79 | 102.36 | 2.92
GA8TAN54800W | 48 | High | 55 | 95 | 52.88 | 111.69 | 3.28
GA8TAN54800W | 48 | High | 55 | 105 | 49.78 | 120.96 | 3.7
GA8TAN54800W | 48 | High | 55 | 115 | 46.51 | 130.24 | 4.18
GA8TAN54800W | 48 | Low | 30 | 55 | 23.74 | 63.25 | 1.39
GA8TAN54800W | 48 | Low | 30 | 65 | 24.01 | 73.31 | 1.58
GA8TAN54800W | 48 | Low | 30 | 75 | 23.49 | 83.18 | 1.79
GA8TAN54800W | 48 | Low | 30 | 85 | 22.24 | 92.88 | 2.02
GA8TAN54800W | 48 | Low | 30 | 95 | 20.28 | 102.42 | 2.29
GA8TAN54800W | 48 | Low | 30 | 105 | 17.68 | 111.81 | 2.58
GA8TAN54800W | 48 | Low | 30 | 115 | 14.53 | 121.03 | 2.91
GA8TAN54800W | 48 | Low | 35 | 55 | 28.01 | 64.37 | 1.35
GA8TAN54800W | 48 | Low | 35 | 65 | 27.71 | 74.26 | 1.55
GA8TAN54800W | 48 | Low | 35 | 75 | 26.79 | 84.02 | 1.76
GA8TAN54800W | 48 | Low | 35 | 85 | 25.28 | 93.64 | 1.99
GA8TAN54800W | 48 | Low | 35 | 95 | 23.18 | 103.15 | 2.26
GA8TAN54800W | 48 | Low | 35 | 105 | 20.52 | 112.52 | 2.55
GA8TAN54800W | 48 | Low | 35 | 115 | 17.37 | 121.78 | 2.88
GA8TAN54800W | 48 | Low | 40 | 55 | 32.43 | 65.52 | 1.31
GA8TAN54800W | 48 | Low | 40 | 65 | 31.61 | 75.26 | 1.51
GA8TAN54800W | 48 | Low | 40 | 75 | 30.35 | 84.9 | 1.73
GA8TAN54800W | 48 | Low | 40 | 85 | 28.6 | 94.47 | 1.96
GA8TAN54800W | 48 | Low | 40 | 95 | 26.39 | 103.97 | 2.23
GA8TAN54800W | 48 | Low | 40 | 105 | 23.69 | 113.32 | 2.52
GA8TAN54800W | 48 | Low | 40 | 115 | 20.56 | 122.59 | 2.85
GA8TAN54800W | 48 | Low | 45 | 55 | 36.93 | 66.7 | 1.27
GA8TAN54800W | 48 | Low | 45 | 65 | 35.67 | 76.31 | 1.48
GA8TAN54800W | 48 | Low | 45 | 75 | 34.09 | 85.86 | 1.69
GA8TAN54800W | 48 | Low | 45 | 85 | 32.16 | 95.36 | 1.93
GA8TAN54800W | 48 | Low | 45 | 95 | 29.85 | 104.82 | 2.2
GA8TAN54800W | 48 | Low | 45 | 105 | 27.16 | 114.2 | 2.49
GA8TAN54800W | 48 | Low | 45 | 115 | 24.08 | 123.48 | 2.82
GA8TAN54800W | 48 | Low | 50 | 55 | 41.5 | 67.9 | 1.23
GA8TAN54800W | 48 | Low | 50 | 65 | 39.85 | 77.38 | 1.44
GA8TAN54800W | 48 | Low | 50 | 75 | 38.01 | 86.85 | 1.66
GA8TAN54800W | 48 | Low | 50 | 85 | 35.95 | 96.22 | 1.9
GA8TAN54800W | 48 | Low | 50 | 95 | 33.57 | 105.75 | 2.17
GA8TAN54800W | 48 | Low | 50 | 105 | 30.92 | 115.14 | 2.46
GA8TAN54800W | 48 | Low | 50 | 115 | 27.94 | 124.47 | 2.79
GA8TAN54800W | 48 | Low | 55 | 55 | 46.08 | 69.11 | 1.18
GA8TAN54800W | 48 | Low | 55 | 65 | 44.1 | 78.48 | 1.39
GA8TAN54800W | 48 | Low | 55 | 75 | 42.06 | 87.88 | 1.62
GA8TAN54800W | 48 | Low | 55 | 85 | 39.88 | 97.29 | 1.86
GA8TAN54800W | 48 | Low | 55 | 95 | 37.5 | 106.73 | 2.13
GA8TAN54800W | 48 | Low | 55 | 105 | 34.89 | 116.14 | 2.43
GA8TAN54800W | 48 | Low | 55 | 115 | 32 | 125.45 | 2.76
GA8TAN56000W | 60 | High | 30 | 55 | 49.68 | 70.09 | 2.49
GA8TAN56000W | 60 | High | 30 | 65 | 47.27 | 79.39 | 2.82
GA8TAN56000W | 60 | High | 30 | 75 | 44.86 | 88.66 | 3.17
GA8TAN56000W | 60 | High | 30 | 85 | 42.46 | 98.04 | 3.56
GA8TAN56000W | 60 | High | 30 | 95 | 39.97 | 107.42 | 4.01
GA8TAN56000W | 60 | High | 30 | 105 | 37.34 | 116.79 | 4.51
GA8TAN56000W | 60 | High | 30 | 115 | 34.52 | 126.14 | 5.08
GA8TAN56000W | 60 | High | 35 | 55 | 54.65 | 71.44 | 2.53
GA8TAN56000W | 60 | High | 35 | 65 | 52.06 | 80.62 | 2.85
GA8TAN56000W | 60 | High | 35 | 75 | 49.48 | 89.88 | 3.2
GA8TAN56000W | 60 | High | 35 | 85 | 46.88 | 99.18 | 3.59
GA8TAN56000W | 60 | High | 35 | 95 | 44.17 | 108.51 | 4.04
GA8TAN56000W | 60 | High | 35 | 105 | 41.29 | 117.81 | 4.54
GA8TAN56000W | 60 | High | 35 | 115 | 38.23 | 127.11 | 5.12
GA8TAN56000W | 60 | High | 40 | 55 | 60.04 | 72.97 | 2.58
GA8TAN56000W | 60 | High | 40 | 65 | 57.25 | 82 | 2.88
GA8TAN56000W | 60 | High | 40 | 75 | 54.48 | 91.2 | 3.23
GA8TAN56000W | 60 | High | 40 | 85 | 51.63 | 100.42 | 3.62
GA8TAN56000W | 60 | High | 40 | 95 | 48.69 | 109.69 | 4.07
GA8TAN56000W | 60 | High | 40 | 105 | 45.55 | 118.94 | 4.58
GA8TAN56000W | 60 | High | 40 | 115 | 42.22 | 128.16 | 5.17
GA8TAN56000W | 60 | High | 45 | 55 | 65.8 | 74.5 | 2.61
GA8TAN56000W | 60 | High | 45 | 65 | 62.82 | 83.5 | 2.92
GA8TAN56000W | 60 | High | 45 | 75 | 59.84 | 92.63 | 3.27
GA8TAN56000W | 60 | High | 45 | 85 | 56.76 | 101.8 | 3.66
GA8TAN56000W | 60 | High | 45 | 95 | 53.54 | 110.97 | 4.11
GA8TAN56000W | 60 | High | 45 | 105 | 50.18 | 120.18 | 4.63
GA8TAN56000W | 60 | High | 45 | 115 | 46.56 | 129.32 | 5.22
GA8TAN56000W | 60 | High | 50 | 55 | 72.02 | 76.22 | 2.66
GA8TAN56000W | 60 | High | 50 | 65 | 68.84 | 85.18 | 2.97
GA8TAN56000W | 60 | High | 50 | 75 | 65.58 | 94.19 | 3.31
GA8TAN56000W | 60 | High | 50 | 85 | 62.25 | 103.27 | 3.7
GA8TAN56000W | 60 | High | 50 | 95 | 58.78 | 112.37 | 4.16
GA8TAN56000W | 60 | High | 50 | 105 | 55.1 | 121.48 | 4.68
GA8TAN56000W | 60 | High | 50 | 115 | 51.14 | 130.5 | 5.28
GA8TAN56000W | 60 | High | 55 | 55 | 78.7 | 78.11 | 2.71
GA8TAN56000W | 60 | High | 55 | 65 | 75.27 | 86.94 | 3.01
GA8TAN56000W | 60 | High | 55 | 75 | 71.76 | 95.86 | 3.35
GA8TAN56000W | 60 | High | 55 | 85 | 68.15 | 104.87 | 3.75
GA8TAN56000W | 60 | High | 55 | 95 | 64.36 | 113.86 | 4.21
GA8TAN56000W | 60 | High | 55 | 105 | 60.36 | 122.85 | 4.74
GA8TAN56000W | 60 | High | 55 | 115 | 56.09 | 131.78 | 5.35
GA8TAN56000W | 60 | Low | 30 | 55 | 31.8 | 65.12 | 1.73
GA8TAN56000W | 60 | Low | 30 | 65 | 30.14 | 74.57 | 1.99
GA8TAN56000W | 60 | Low | 30 | 75 | 28.52 | 84.1 | 2.26
GA8TAN56000W | 60 | Low | 30 | 85 | 26.86 | 93.65 | 2.55
GA8TAN56000W | 60 | Low | 30 | 95 | 25 | 103.15 | 2.86
GA8TAN56000W | 60 | Low | 30 | 105 | 22.92 | 112.63 | 3.2
GA8TAN56000W | 60 | Low | 30 | 115 | 20.53 | 122.05 | 3.57
GA8TAN56000W | 60 | Low | 35 | 55 | 35.17 | 66 | 1.68
GA8TAN56000W | 60 | Low | 35 | 65 | 33.47 | 75.42 | 1.94
GA8TAN56000W | 60 | Low | 35 | 75 | 31.81 | 84.91 | 2.22
GA8TAN56000W | 60 | Low | 35 | 85 | 30.06 | 94.44 | 2.52
GA8TAN56000W | 60 | Low | 35 | 95 | 28.14 | 103.92 | 2.83
GA8TAN56000W | 60 | Low | 35 | 105 | 25.93 | 113.36 | 3.17
GA8TAN56000W | 60 | Low | 35 | 115 | 23.41 | 122.75 | 3.55
GA8TAN56000W | 60 | Low | 40 | 55 | 38.82 | 66.96 | 1.62
GA8TAN56000W | 60 | Low | 40 | 65 | 37.09 | 76.35 | 1.89
GA8TAN56000W | 60 | Low | 40 | 75 | 35.37 | 85.81 | 2.18
GA8TAN56000W | 60 | Low | 40 | 85 | 33.55 | 95.29 | 2.48
GA8TAN56000W | 60 | Low | 40 | 95 | 31.5 | 104.76 | 2.8
GA8TAN56000W | 60 | Low | 40 | 105 | 29.2 | 114.16 | 3.14
GA8TAN56000W | 60 | Low | 40 | 115 | 26.53 | 123.5 | 3.52
GA8TAN56000W | 60 | Low | 45 | 55 | 42.8 | 68.02 | 1.57
GA8TAN56000W | 60 | Low | 45 | 65 | 41.03 | 77.4 | 1.85
GA8TAN56000W | 60 | Low | 45 | 75 | 39.25 | 86.79 | 2.13
GA8TAN56000W | 60 | Low | 45 | 85 | 37.34 | 96.23 | 2.44
GA8TAN56000W | 60 | Low | 45 | 95 | 35.19 | 105.66 | 2.76
GA8TAN56000W | 60 | Low | 45 | 105 | 32.74 | 115.01 | 3.11
GA8TAN56000W | 60 | Low | 45 | 115 | 29.92 | 124.31 | 3.49
GA8TAN56000W | 60 | Low | 50 | 55 | 47.13 | 69.16 | 1.51
GA8TAN56000W | 60 | Low | 50 | 65 | 45.33 | 78.49 | 1.8
GA8TAN56000W | 60 | Low | 50 | 75 | 43.47 | 87.85 | 2.09
GA8TAN56000W | 60 | Low | 50 | 85 | 41.47 | 97.27 | 2.4
GA8TAN56000W | 60 | Low | 50 | 95 | 39.18 | 106.62 | 2.73
GA8TAN56000W | 60 | Low | 50 | 105 | 36.59 | 115.94 | 3.08
GA8TAN56000W | 60 | Low | 50 | 115 | 33.65 | 125.23 | 3.46
GA8TAN56000W | 60 | Low | 55 | 55 | 51.9 | 70.47 | 1.47
GA8TAN56000W | 60 | Low | 55 | 65 | 50 | 79.67 | 1.75
GA8TAN56000W | 60 | Low | 55 | 75 | 48.08 | 89.04 | 2.05
GA8TAN56000W | 60 | Low | 55 | 85 | 45.93 | 98.36 | 2.36
GA8TAN56000W | 60 | Low | 55 | 95 | 43.54 | 107.69 | 2.69
GA8TAN56000W | 60 | Low | 55 | 105 | 40.77 | 116.94 | 3.05
GA8TAN56000W | 60 | Low | 55 | 115 | 37.59 | 126.16 | 3.43

## GH5_Detail_Cool
ODU_Model | IDU_Model | Size_Nom | CFM | EWB_F | ODB_F | TC_Net_kBtu | Sens_Net_kBtu | Sys_kW
GH5SAN51800A | FJ5AN*A18L | 18 | 540 | 72 | 75 | 20.56 | 10.51 | 1.16
GH5SAN51800A | FJ5AN*A18L | 18 | 540 | 72 | 85 | 19.66 | 10.18 | 1.31
GH5SAN51800A | FJ5AN*A18L | 18 | 540 | 72 | 95 | 18.67 | 9.82 | 1.47
GH5SAN51800A | FJ5AN*A18L | 18 | 540 | 72 | 105 | 17.45 | 9.38 | 1.64
GH5SAN51800A | FJ5AN*A18L | 18 | 540 | 72 | 115 | 16.46 | 9.04 | 1.84
GH5SAN51800A | FJ5AN*A18L | 18 | 540 | 72 | 125 | 15.26 | 8.62 | 2.06
GH5SAN51800A | FJ5AN*A18L | 18 | 540 | 67 | 75 | 18.72 | 13.04 | 1.17
GH5SAN51800A | FJ5AN*A18L | 18 | 540 | 67 | 85 | 17.91 | 12.71 | 1.32
GH5SAN51800A | FJ5AN*A18L | 18 | 540 | 67 | 95 | 17 | 12.35 | 1.48
GH5SAN51800A | FJ5AN*A18L | 18 | 540 | 67 | 105 | 16.02 | 11.95 | 1.65
GH5SAN51800A | FJ5AN*A18L | 18 | 540 | 67 | 115 | 15.01 | 11.56 | 1.85
GH5SAN51800A | FJ5AN*A18L | 18 | 540 | 67 | 125 | 13.93 | 11.13 | 2.07
GH5SAN51800A | FJ5AN*A18L | 18 | 540 | 62 | 75 | 17.16 | 15.51 | 1.18
GH5SAN51800A | FJ5AN*A18L | 18 | 540 | 62 | 85 | 16.43 | 15.16 | 1.33
GH5SAN51800A | FJ5AN*A18L | 18 | 540 | 62 | 95 | 15.64 | 14.77 | 1.48
GH5SAN51800A | FJ5AN*A18L | 18 | 540 | 62 | 105 | 14.82 | 14.82 | 1.66
GH5SAN51800A | FJ5AN*A18L | 18 | 540 | 62 | 115 | 14.02 | 14.02 | 1.85
GH5SAN51800A | FJ5AN*A18L | 18 | 540 | 62 | 125 | 13.18 | 13.18 | 2.07
GH5SAN51800A | FJ5AN*A18L | 18 | 600 | 72 | 75 | 20.83 | 10.93 | 1.17
GH5SAN51800A | FJ5AN*A18L | 18 | 600 | 72 | 85 | 19.9 | 10.59 | 1.32
GH5SAN51800A | FJ5AN*A18L | 18 | 600 | 72 | 95 | 18.88 | 10.23 | 1.48
GH5SAN51800A | FJ5AN*A18L | 18 | 600 | 72 | 105 | 17.78 | 9.85 | 1.66
GH5SAN51800A | FJ5AN*A18L | 18 | 600 | 72 | 115 | 16.61 | 9.45 | 1.85
GH5SAN51800A | FJ5AN*A18L | 18 | 600 | 72 | 125 | 15.36 | 9.01 | 2.08
GH5SAN51800A | FJ5AN*A18L | 18 | 600 | 67 | 75 | 18.99 | 13.73 | 1.19
GH5SAN51800A | FJ5AN*A18L | 18 | 600 | 67 | 85 | 18.15 | 13.39 | 1.33
GH5SAN51800A | FJ5AN*A18L | 18 | 600 | 67 | 95 | 17.22 | 13.02 | 1.49
GH5SAN51800A | FJ5AN*A18L | 18 | 600 | 67 | 105 | 16.22 | 12.63 | 1.67
GH5SAN51800A | FJ5AN*A18L | 18 | 600 | 67 | 115 | 15.18 | 12.21 | 1.86
GH5SAN51800A | FJ5AN*A18L | 18 | 600 | 67 | 125 | 14.07 | 11.78 | 2.09
GH5SAN51800A | FJ5AN*A18L | 18 | 600 | 62 | 75 | 17.5 | 16.41 | 1.19
GH5SAN51800A | FJ5AN*A18L | 18 | 600 | 62 | 85 | 16.76 | 16.03 | 1.34
GH5SAN51800A | FJ5AN*A18L | 18 | 600 | 62 | 95 | 15.99 | 15.99 | 1.5
GH5SAN51800A | FJ5AN*A18L | 18 | 600 | 62 | 105 | 15.13 | 15.13 | 1.67
GH5SAN51800A | FJ5AN*A18L | 18 | 600 | 62 | 115 | 14.41 | 14.41 | 1.87
GH5SAN51800A | FJ5AN*A18L | 18 | 600 | 62 | 125 | 13.53 | 13.53 | 2.09
GH5SAN51800A | FJ5AN*A18L | 18 | 675 | 72 | 75 | 21.1 | 11.43 | 1.19
GH5SAN51800A | FJ5AN*A18L | 18 | 675 | 72 | 85 | 20.14 | 11.09 | 1.34
GH5SAN51800A | FJ5AN*A18L | 18 | 675 | 72 | 95 | 19.08 | 10.73 | 1.5
GH5SAN51800A | FJ5AN*A18L | 18 | 675 | 72 | 105 | 17.95 | 10.33 | 1.68
GH5SAN51800A | FJ5AN*A18L | 18 | 675 | 72 | 115 | 16.75 | 9.93 | 1.87
GH5SAN51800A | FJ5AN*A18L | 18 | 675 | 72 | 125 | 15.49 | 9.5 | 2.1
GH5SAN51800A | FJ5AN*A18L | 18 | 675 | 67 | 75 | 19.26 | 14.55 | 1.2
GH5SAN51800A | FJ5AN*A18L | 18 | 675 | 67 | 85 | 18.39 | 14.21 | 1.35
GH5SAN51800A | FJ5AN*A18L | 18 | 675 | 67 | 95 | 17.43 | 13.83 | 1.51
GH5SAN51800A | FJ5AN*A18L | 18 | 675 | 67 | 105 | 16.41 | 13.44 | 1.69
GH5SAN51800A | FJ5AN*A18L | 18 | 675 | 67 | 115 | 15.33 | 13.01 | 1.88
GH5SAN51800A | FJ5AN*A18L | 18 | 675 | 67 | 125 | 14.21 | 12.55 | 2.1
GH5SAN51800A | FJ5AN*A18L | 18 | 675 | 62 | 75 | 17.91 | 17.91 | 1.21
GH5SAN51800A | FJ5AN*A18L | 18 | 675 | 62 | 85 | 17.24 | 17.24 | 1.36
GH5SAN51800A | FJ5AN*A18L | 18 | 675 | 62 | 95 | 16.49 | 16.49 | 1.52
GH5SAN51800A | FJ5AN*A18L | 18 | 675 | 62 | 105 | 15.68 | 15.68 | 1.69
GH5SAN51800A | FJ5AN*A18L | 18 | 675 | 62 | 115 | 14.77 | 14.77 | 1.88
GH5SAN51800A | FJ5AN*A18L | 18 | 675 | 62 | 125 | 13.88 | 13.88 | 2.11
GH5SAN52400A | FJ5AN*B24L | 24 | 665 | 72 | 75 | 26.92 | 13.97 | 1.47
GH5SAN52400A | FJ5AN*B24L | 24 | 665 | 72 | 85 | 25.78 | 13.53 | 1.65
GH5SAN52400A | FJ5AN*B24L | 24 | 665 | 72 | 95 | 24.57 | 13.07 | 1.85
GH5SAN52400A | FJ5AN*B24L | 24 | 665 | 72 | 105 | 23.28 | 12.59 | 2.09
GH5SAN52400A | FJ5AN*B24L | 24 | 665 | 72 | 115 | 21.88 | 12.06 | 2.35
GH5SAN52400A | FJ5AN*B24L | 24 | 665 | 72 | 125 | 20.37 | 11.5 | 2.64
GH5SAN52400A | FJ5AN*B24L | 24 | 665 | 67 | 75 | 24.56 | 17.17 | 1.48
GH5SAN52400A | FJ5AN*B24L | 24 | 665 | 67 | 85 | 23.51 | 16.72 | 1.66
GH5SAN52400A | FJ5AN*B24L | 24 | 665 | 67 | 95 | 22.4 | 16.25 | 1.87
GH5SAN52400A | FJ5AN*B24L | 24 | 665 | 67 | 105 | 21.2 | 15.74 | 2.1
GH5SAN52400A | FJ5AN*B24L | 24 | 665 | 67 | 115 | 19.95 | 15.23 | 2.36
GH5SAN52400A | FJ5AN*B24L | 24 | 665 | 67 | 125 | 18.57 | 14.66 | 2.66
GH5SAN52400A | FJ5AN*B24L | 24 | 665 | 62 | 75 | 22.46 | 20.29 | 1.49
GH5SAN52400A | FJ5AN*B24L | 24 | 665 | 62 | 85 | 21.5 | 19.83 | 1.67
GH5SAN52400A | FJ5AN*B24L | 24 | 665 | 62 | 95 | 20.51 | 19.34 | 1.88
GH5SAN52400A | FJ5AN*B24L | 24 | 665 | 62 | 105 | 19.46 | 18.82 | 2.11
GH5SAN52400A | FJ5AN*B24L | 24 | 665 | 62 | 115 | 18.35 | 18.23 | 2.37
GH5SAN52400A | FJ5AN*B24L | 24 | 665 | 62 | 125 | 17.24 | 17.24 | 2.67
GH5SAN52400A | FJ5AN*B24L | 24 | 800 | 72 | 75 | 27.58 | 14.93 | 1.5
GH5SAN52400A | FJ5AN*B24L | 24 | 800 | 72 | 85 | 26.37 | 14.48 | 1.68
GH5SAN52400A | FJ5AN*B24L | 24 | 800 | 72 | 95 | 25.1 | 14.01 | 1.89
GH5SAN52400A | FJ5AN*B24L | 24 | 800 | 72 | 105 | 23.74 | 13.51 | 2.12
GH5SAN52400A | FJ5AN*B24L | 24 | 800 | 72 | 115 | 22.27 | 12.98 | 2.38
GH5SAN52400A | FJ5AN*B24L | 24 | 800 | 72 | 125 | 20.68 | 12.41 | 2.67
GH5SAN52400A | FJ5AN*B24L | 24 | 800 | 67 | 75 | 25.21 | 18.75 | 1.51
GH5SAN52400A | FJ5AN*B24L | 24 | 800 | 67 | 85 | 24.1 | 18.29 | 1.69
GH5SAN52400A | FJ5AN*B24L | 24 | 800 | 67 | 95 | 22.94 | 17.81 | 1.9
GH5SAN52400A | FJ5AN*B24L | 24 | 800 | 67 | 105 | 21.69 | 17.31 | 2.13
GH5SAN52400A | FJ5AN*B24L | 24 | 800 | 67 | 115 | 20.37 | 16.74 | 2.39
GH5SAN52400A | FJ5AN*B24L | 24 | 800 | 67 | 125 | 18.95 | 16.16 | 2.69
GH5SAN52400A | FJ5AN*B24L | 24 | 800 | 62 | 75 | 23.23 | 22.42 | 1.52
GH5SAN52400A | FJ5AN*B24L | 24 | 800 | 62 | 85 | 22.25 | 21.9 | 1.7
GH5SAN52400A | FJ5AN*B24L | 24 | 800 | 62 | 95 | 21.3 | 21.17 | 1.91
GH5SAN52400A | FJ5AN*B24L | 24 | 800 | 62 | 105 | 20.27 | 20.27 | 2.14
GH5SAN52400A | FJ5AN*B24L | 24 | 800 | 62 | 115 | 19.23 | 19.23 | 2.4
GH5SAN52400A | FJ5AN*B24L | 24 | 800 | 62 | 125 | 18.1 | 18.1 | 2.69
GH5SAN52400A | FJ5AN*B24L | 24 | 900 | 72 | 75 | 27.91 | 15.6 | 1.52
GH5SAN52400A | FJ5AN*B24L | 24 | 900 | 72 | 85 | 26.68 | 15.15 | 1.7
GH5SAN52400A | FJ5AN*B24L | 24 | 900 | 72 | 95 | 25.36 | 14.67 | 1.91
GH5SAN52400A | FJ5AN*B24L | 24 | 900 | 72 | 105 | 23.97 | 14.17 | 2.14
GH5SAN52400A | FJ5AN*B24L | 24 | 900 | 72 | 115 | 22.46 | 13.63 | 2.4
GH5SAN52400A | FJ5AN*B24L | 24 | 900 | 72 | 125 | 20.82 | 13.06 | 2.7
GH5SAN52400A | FJ5AN*B24L | 24 | 900 | 67 | 75 | 25.56 | 19.86 | 1.54
GH5SAN52400A | FJ5AN*B24L | 24 | 900 | 67 | 85 | 24.42 | 19.39 | 1.72
GH5SAN52400A | FJ5AN*B24L | 24 | 900 | 67 | 95 | 23.22 | 18.9 | 1.92
GH5SAN52400A | FJ5AN*B24L | 24 | 900 | 67 | 105 | 21.94 | 18.39 | 2.15
GH5SAN52400A | FJ5AN*B24L | 24 | 900 | 67 | 115 | 20.58 | 17.82 | 2.42
GH5SAN52400A | FJ5AN*B24L | 24 | 900 | 67 | 125 | 19.11 | 17.22 | 2.71
GH5SAN52400A | FJ5AN*B24L | 24 | 900 | 62 | 75 | 23.75 | 23.75 | 1.55
GH5SAN52400A | FJ5AN*B24L | 24 | 900 | 62 | 85 | 22.82 | 22.82 | 1.72
GH5SAN52400A | FJ5AN*B24L | 24 | 900 | 62 | 95 | 21.88 | 21.88 | 1.93
GH5SAN52400A | FJ5AN*B24L | 24 | 900 | 62 | 105 | 20.87 | 20.87 | 2.16
GH5SAN52400A | FJ5AN*B24L | 24 | 900 | 62 | 115 | 19.78 | 19.78 | 2.42
GH5SAN52400A | FJ5AN*B24L | 24 | 900 | 62 | 125 | 18.58 | 18.58 | 2.72
GH5SAN53000A | FJ5AN*B30L | 30 | 915 | 72 | 75 | 34.58 | 18.36 | 1.89
GH5SAN53000A | FJ5AN*B30L | 30 | 915 | 72 | 85 | 33 | 17.76 | 2.13
GH5SAN53000A | FJ5AN*B30L | 30 | 915 | 72 | 95 | 31.31 | 17.13 | 2.39
GH5SAN53000A | FJ5AN*B30L | 30 | 915 | 72 | 105 | 29.54 | 16.47 | 2.68
GH5SAN53000A | FJ5AN*B30L | 30 | 915 | 72 | 115 | 27.68 | 15.79 | 3.01
GH5SAN53000A | FJ5AN*B30L | 30 | 915 | 72 | 125 | 25.76 | 15.1 | 3.4
GH5SAN53000A | FJ5AN*B30L | 30 | 915 | 67 | 75 | 31.39 | 22.78 | 1.88
GH5SAN53000A | FJ5AN*B30L | 30 | 915 | 67 | 85 | 29.94 | 22.17 | 2.11
GH5SAN53000A | FJ5AN*B30L | 30 | 915 | 67 | 95 | 28.4 | 21.53 | 2.37
GH5SAN53000A | FJ5AN*B30L | 30 | 915 | 67 | 105 | 26.78 | 20.87 | 2.65
GH5SAN53000A | FJ5AN*B30L | 30 | 915 | 67 | 115 | 25.09 | 20.18 | 2.98
GH5SAN53000A | FJ5AN*B30L | 30 | 915 | 67 | 125 | 23.34 | 19.47 | 3.36
GH5SAN53000A | FJ5AN*B30L | 30 | 915 | 62 | 75 | 28.7 | 27.11 | 1.87
GH5SAN53000A | FJ5AN*B30L | 30 | 915 | 62 | 85 | 27.4 | 26.47 | 2.1
GH5SAN53000A | FJ5AN*B30L | 30 | 915 | 62 | 95 | 26.05 | 25.76 | 2.35
GH5SAN53000A | FJ5AN*B30L | 30 | 915 | 62 | 105 | 24.68 | 24.68 | 2.63
GH5SAN53000A | FJ5AN*B30L | 30 | 915 | 62 | 115 | 23.4 | 23.4 | 2.96
GH5SAN53000A | FJ5AN*B30L | 30 | 915 | 62 | 125 | 21.89 | 21.89 | 3.34
GH5SAN53000A | FJ5AN*B30L | 30 | 1000 | 72 | 75 | 34.98 | 18.98 | 1.92
GH5SAN53000A | FJ5AN*B30L | 30 | 1000 | 72 | 85 | 33.35 | 18.37 | 2.16
GH5SAN53000A | FJ5AN*B30L | 30 | 1000 | 72 | 95 | 31.62 | 17.73 | 2.42
GH5SAN53000A | FJ5AN*B30L | 30 | 1000 | 72 | 105 | 29.83 | 17.08 | 2.7
GH5SAN53000A | FJ5AN*B30L | 30 | 1000 | 72 | 115 | 27.93 | 16.4 | 3.04
GH5SAN53000A | FJ5AN*B30L | 30 | 1000 | 72 | 125 | 25.94 | 15.69 | 3.43
GH5SAN53000A | FJ5AN*B30L | 30 | 1000 | 67 | 75 | 31.78 | 23.8 | 1.91
GH5SAN53000A | FJ5AN*B30L | 30 | 1000 | 67 | 85 | 30.3 | 23.19 | 2.14
GH5SAN53000A | FJ5AN*B30L | 30 | 1000 | 67 | 95 | 28.72 | 22.54 | 2.39
GH5SAN53000A | FJ5AN*B30L | 30 | 1000 | 67 | 105 | 27.06 | 21.85 | 2.68
GH5SAN53000A | FJ5AN*B30L | 30 | 1000 | 67 | 115 | 25.35 | 21.13 | 3
GH5SAN53000A | FJ5AN*B30L | 30 | 1000 | 67 | 125 | 23.55 | 20.44 | 3.39
GH5SAN53000A | FJ5AN*B30L | 30 | 1000 | 62 | 75 | 29.19 | 28.46 | 1.9
GH5SAN53000A | FJ5AN*B30L | 30 | 1000 | 62 | 85 | 27.89 | 27.75 | 2.13
GH5SAN53000A | FJ5AN*B30L | 30 | 1000 | 62 | 95 | 26.7 | 26.54 | 2.38
GH5SAN53000A | FJ5AN*B30L | 30 | 1000 | 62 | 105 | 25.32 | 25.32 | 2.66
GH5SAN53000A | FJ5AN*B30L | 30 | 1000 | 62 | 115 | 23.98 | 23.98 | 2.99
GH5SAN53000A | FJ5AN*B30L | 30 | 1000 | 62 | 125 | 22.57 | 22.57 | 3.38
GH5SAN53000A | FJ5AN*B30L | 30 | 1125 | 72 | 75 | 35.44 | 19.85 | 1.96
GH5SAN53000A | FJ5AN*B30L | 30 | 1125 | 72 | 85 | 33.76 | 19.24 | 2.2
GH5SAN53000A | FJ5AN*B30L | 30 | 1125 | 72 | 95 | 31.98 | 18.6 | 2.46
GH5SAN53000A | FJ5AN*B30L | 30 | 1125 | 72 | 105 | 30.14 | 17.94 | 2.75
GH5SAN53000A | FJ5AN*B30L | 30 | 1125 | 72 | 115 | 28.19 | 17.25 | 3.08
GH5SAN53000A | FJ5AN*B30L | 30 | 1125 | 72 | 125 | 26.15 | 16.56 | 3.47
GH5SAN53000A | FJ5AN*B30L | 30 | 1125 | 67 | 75 | 32.24 | 25.25 | 1.95
GH5SAN53000A | FJ5AN*B30L | 30 | 1125 | 67 | 85 | 30.71 | 24.62 | 2.18
GH5SAN53000A | FJ5AN*B30L | 30 | 1125 | 67 | 95 | 29.09 | 23.96 | 2.43
GH5SAN53000A | FJ5AN*B30L | 30 | 1125 | 67 | 105 | 27.39 | 23.27 | 2.72
GH5SAN53000A | FJ5AN*B30L | 30 | 1125 | 67 | 115 | 25.63 | 22.55 | 3.05
GH5SAN53000A | FJ5AN*B30L | 30 | 1125 | 67 | 125 | 23.81 | 21.79 | 3.43
GH5SAN53000A | FJ5AN*B30L | 30 | 1125 | 62 | 75 | 29.99 | 29.87 | 1.94
GH5SAN53000A | FJ5AN*B30L | 30 | 1125 | 62 | 85 | 28.7 | 28.7 | 2.17
GH5SAN53000A | FJ5AN*B30L | 30 | 1125 | 62 | 95 | 27.44 | 27.44 | 2.42
GH5SAN53000A | FJ5AN*B30L | 30 | 1125 | 62 | 105 | 26.1 | 26.1 | 2.71
GH5SAN53000A | FJ5AN*B30L | 30 | 1125 | 62 | 115 | 24.7 | 24.7 | 3.04
GH5SAN53000A | FJ5AN*B30L | 30 | 1125 | 62 | 125 | 23.21 | 23.21 | 3.43
GH5SAN53600A | FJ5AN*B36L | 36 | 1050 | 72 | 75 | 42.54 | 21.74 | 2.43
GH5SAN53600A | FJ5AN*B36L | 36 | 1050 | 72 | 85 | 40.63 | 21.02 | 2.66
GH5SAN53600A | FJ5AN*B36L | 36 | 1050 | 72 | 95 | 38.54 | 20.24 | 2.91
GH5SAN53600A | FJ5AN*B36L | 36 | 1050 | 72 | 105 | 36.29 | 19.42 | 3.21
GH5SAN53600A | FJ5AN*B36L | 36 | 1050 | 72 | 115 | 33.89 | 18.55 | 3.55
GH5SAN53600A | FJ5AN*B36L | 36 | 1050 | 72 | 125 | 31.34 | 17.65 | 3.95
GH5SAN53600A | FJ5AN*B36L | 36 | 1050 | 67 | 75 | 38.6 | 26.83 | 2.41
GH5SAN53600A | FJ5AN*B36L | 36 | 1050 | 67 | 85 | 36.9 | 26.13 | 2.65
GH5SAN53600A | FJ5AN*B36L | 36 | 1050 | 67 | 95 | 35 | 25.34 | 2.92
GH5SAN53600A | FJ5AN*B36L | 36 | 1050 | 67 | 105 | 32.95 | 24.51 | 3.22
GH5SAN53600A | FJ5AN*B36L | 36 | 1050 | 67 | 115 | 30.77 | 23.63 | 3.57
GH5SAN53600A | FJ5AN*B36L | 36 | 1050 | 67 | 125 | 28.49 | 22.72 | 3.98
GH5SAN53600A | FJ5AN*B36L | 36 | 1050 | 62 | 75 | 35.27 | 31.84 | 2.4
GH5SAN53600A | FJ5AN*B36L | 36 | 1050 | 62 | 85 | 33.74 | 31.1 | 2.64
GH5SAN53600A | FJ5AN*B36L | 36 | 1050 | 62 | 95 | 32.06 | 30.28 | 2.91
GH5SAN53600A | FJ5AN*B36L | 36 | 1050 | 62 | 105 | 30.27 | 29.35 | 3.22
GH5SAN53600A | FJ5AN*B36L | 36 | 1050 | 62 | 115 | 28.48 | 28.48 | 3.58
GH5SAN53600A | FJ5AN*B36L | 36 | 1050 | 62 | 125 | 26.75 | 26.75 | 3.98
GH5SAN53600A | FJ5AN*B36L | 36 | 1200 | 72 | 75 | 43.29 | 22.8 | 2.48
GH5SAN53600A | FJ5AN*B36L | 36 | 1200 | 72 | 85 | 41.3 | 22.07 | 2.71
GH5SAN53600A | FJ5AN*B36L | 36 | 1200 | 72 | 95 | 39.11 | 21.28 | 2.96
GH5SAN53600A | FJ5AN*B36L | 36 | 1200 | 72 | 105 | 36.78 | 20.44 | 3.25
GH5SAN53600A | FJ5AN*B36L | 36 | 1200 | 72 | 115 | 34.24 | 19.52 | 3.59
GH5SAN53600A | FJ5AN*B36L | 36 | 1200 | 72 | 125 | 31.66 | 18.65 | 3.99
GH5SAN53600A | FJ5AN*B36L | 36 | 1200 | 67 | 75 | 39.32 | 28.59 | 2.47
GH5SAN53600A | FJ5AN*B36L | 36 | 1200 | 67 | 85 | 37.55 | 27.87 | 2.71
GH5SAN53600A | FJ5AN*B36L | 36 | 1200 | 67 | 95 | 35.57 | 27.07 | 2.97
GH5SAN53600A | FJ5AN*B36L | 36 | 1200 | 67 | 105 | 33.44 | 26.21 | 3.27
GH5SAN53600A | FJ5AN*B36L | 36 | 1200 | 67 | 115 | 31.19 | 25.31 | 3.62
GH5SAN53600A | FJ5AN*B36L | 36 | 1200 | 67 | 125 | 28.84 | 24.37 | 4.03
GH5SAN53600A | FJ5AN*B36L | 36 | 1200 | 62 | 75 | 36.12 | 34.17 | 2.45
GH5SAN53600A | FJ5AN*B36L | 36 | 1200 | 62 | 85 | 34.56 | 33.35 | 2.7
GH5SAN53600A | FJ5AN*B36L | 36 | 1200 | 62 | 95 | 32.98 | 32.1 | 2.97
GH5SAN53600A | FJ5AN*B36L | 36 | 1200 | 62 | 105 | 31.23 | 31.23 | 3.27
GH5SAN53600A | FJ5AN*B36L | 36 | 1200 | 62 | 115 | 29.49 | 29.49 | 3.63
GH5SAN53600A | FJ5AN*B36L | 36 | 1200 | 62 | 125 | 27.63 | 27.63 | 4.04
GH5SAN53600A | FJ5AN*B36L | 36 | 1350 | 72 | 75 | 43.84 | 23.81 | 2.54
GH5SAN53600A | FJ5AN*B36L | 36 | 1350 | 72 | 85 | 41.78 | 23.07 | 2.76
GH5SAN53600A | FJ5AN*B36L | 36 | 1350 | 72 | 95 | 39.53 | 22.27 | 3.02
GH5SAN53600A | FJ5AN*B36L | 36 | 1350 | 72 | 105 | 37.12 | 21.42 | 3.3
GH5SAN53600A | FJ5AN*B36L | 36 | 1350 | 72 | 115 | 34.56 | 20.53 | 3.64
GH5SAN53600A | FJ5AN*B36L | 36 | 1350 | 72 | 125 | 31.85 | 19.6 | 4.04
GH5SAN53600A | FJ5AN*B36L | 36 | 1350 | 67 | 75 | 39.87 | 30.27 | 2.52
GH5SAN53600A | FJ5AN*B36L | 36 | 1350 | 67 | 85 | 38.02 | 29.52 | 2.76
GH5SAN53600A | FJ5AN*B36L | 36 | 1350 | 67 | 95 | 36 | 28.71 | 3.02
GH5SAN53600A | FJ5AN*B36L | 36 | 1350 | 67 | 105 | 33.81 | 27.83 | 3.32
GH5SAN53600A | FJ5AN*B36L | 36 | 1350 | 67 | 115 | 31.49 | 26.9 | 3.66
GH5SAN53600A | FJ5AN*B36L | 36 | 1350 | 67 | 125 | 29.11 | 25.93 | 4.07
GH5SAN53600A | FJ5AN*B36L | 36 | 1350 | 62 | 75 | 36.91 | 36.91 | 2.51
GH5SAN53600A | FJ5AN*B36L | 36 | 1350 | 62 | 85 | 35.43 | 35.43 | 2.75
GH5SAN53600A | FJ5AN*B36L | 36 | 1350 | 62 | 95 | 33.86 | 33.86 | 3.02
GH5SAN53600A | FJ5AN*B36L | 36 | 1350 | 62 | 105 | 32.15 | 32.15 | 3.32
GH5SAN53600A | FJ5AN*B36L | 36 | 1350 | 62 | 115 | 30.3 | 30.3 | 3.67
GH5SAN53600A | FJ5AN*B36L | 36 | 1350 | 62 | 125 | 28.32 | 28.32 | 4.08
GH5SAN54200A | FJ5AN*C42L | 42 | 1240 | 72 | 75 | 49.41 | 25.83 | 2.78
GH5SAN54200A | FJ5AN*C42L | 42 | 1240 | 72 | 85 | 47.34 | 25.04 | 3.09
GH5SAN54200A | FJ5AN*C42L | 42 | 1240 | 72 | 95 | 45.14 | 24.21 | 3.44
GH5SAN54200A | FJ5AN*C42L | 42 | 1240 | 72 | 105 | 42.71 | 23.31 | 3.84
GH5SAN54200A | FJ5AN*C42L | 42 | 1240 | 72 | 115 | 40.15 | 22.37 | 4.3
GH5SAN54200A | FJ5AN*C42L | 42 | 1240 | 72 | 125 | 37.39 | 21.37 | 4.83
GH5SAN54200A | FJ5AN*C42L | 42 | 1240 | 67 | 75 | 44.91 | 31.96 | 2.76
GH5SAN54200A | FJ5AN*C42L | 42 | 1240 | 67 | 85 | 43.04 | 31.17 | 3.07
GH5SAN54200A | FJ5AN*C42L | 42 | 1240 | 67 | 95 | 41 | 30.32 | 3.42
GH5SAN54200A | FJ5AN*C42L | 42 | 1240 | 67 | 105 | 38.8 | 29.41 | 3.82
GH5SAN54200A | FJ5AN*C42L | 42 | 1240 | 67 | 115 | 36.47 | 28.46 | 4.28
GH5SAN54200A | FJ5AN*C42L | 42 | 1240 | 67 | 125 | 33.98 | 27.45 | 4.81
GH5SAN54200A | FJ5AN*C42L | 42 | 1240 | 62 | 75 | 41.08 | 37.94 | 2.74
GH5SAN54200A | FJ5AN*C42L | 42 | 1240 | 62 | 85 | 39.42 | 37.12 | 3.05
GH5SAN54200A | FJ5AN*C42L | 42 | 1240 | 62 | 95 | 37.62 | 36.21 | 3.4
GH5SAN54200A | FJ5AN*C42L | 42 | 1240 | 62 | 105 | 35.72 | 35.01 | 3.8
GH5SAN54200A | FJ5AN*C42L | 42 | 1240 | 62 | 115 | 33.78 | 33.78 | 4.26
GH5SAN54200A | FJ5AN*C42L | 42 | 1240 | 62 | 125 | 31.87 | 31.87 | 4.79
GH5SAN54200A | FJ5AN*C42L | 42 | 1400 | 72 | 75 | 50.19 | 26.99 | 2.83
GH5SAN54200A | FJ5AN*C42L | 42 | 1400 | 72 | 85 | 48.05 | 26.19 | 3.14
GH5SAN54200A | FJ5AN*C42L | 42 | 1400 | 72 | 95 | 45.75 | 25.34 | 3.49
GH5SAN54200A | FJ5AN*C42L | 42 | 1400 | 72 | 105 | 43.26 | 24.44 | 3.89
GH5SAN54200A | FJ5AN*C42L | 42 | 1400 | 72 | 115 | 40.6 | 23.48 | 4.35
GH5SAN54200A | FJ5AN*C42L | 42 | 1400 | 72 | 125 | 37.75 | 22.47 | 4.88
GH5SAN54200A | FJ5AN*C42L | 42 | 1400 | 67 | 75 | 45.66 | 33.86 | 2.81
GH5SAN54200A | FJ5AN*C42L | 42 | 1400 | 67 | 85 | 43.72 | 33.05 | 3.12
GH5SAN54200A | FJ5AN*C42L | 42 | 1400 | 67 | 95 | 41.61 | 32.19 | 3.47
GH5SAN54200A | FJ5AN*C42L | 42 | 1400 | 67 | 105 | 39.35 | 31.26 | 3.87
GH5SAN54200A | FJ5AN*C42L | 42 | 1400 | 67 | 115 | 36.94 | 30.28 | 4.33
GH5SAN54200A | FJ5AN*C42L | 42 | 1400 | 67 | 125 | 34.38 | 29.24 | 4.86
GH5SAN54200A | FJ5AN*C42L | 42 | 1400 | 62 | 75 | 42 | 40.44 | 2.79
GH5SAN54200A | FJ5AN*C42L | 42 | 1400 | 62 | 85 | 40.31 | 39.53 | 3.1
GH5SAN54200A | FJ5AN*C42L | 42 | 1400 | 62 | 95 | 38.59 | 38.26 | 3.45
GH5SAN54200A | FJ5AN*C42L | 42 | 1400 | 62 | 105 | 36.8 | 36.63 | 3.85
GH5SAN54200A | FJ5AN*C42L | 42 | 1400 | 62 | 115 | 34.87 | 34.87 | 4.32
GH5SAN54200A | FJ5AN*C42L | 42 | 1400 | 62 | 125 | 32.86 | 32.86 | 4.85
GH5SAN54200A | FJ5AN*C42L | 42 | 1575 | 72 | 75 | 50.83 | 28.19 | 2.88
GH5SAN54200A | FJ5AN*C42L | 42 | 1575 | 72 | 85 | 48.62 | 27.38 | 3.19
GH5SAN54200A | FJ5AN*C42L | 42 | 1575 | 72 | 95 | 46.25 | 26.53 | 3.54
GH5SAN54200A | FJ5AN*C42L | 42 | 1575 | 72 | 105 | 43.66 | 25.6 | 3.94
GH5SAN54200A | FJ5AN*C42L | 42 | 1575 | 72 | 115 | 40.94 | 24.64 | 4.4
GH5SAN54200A | FJ5AN*C42L | 42 | 1575 | 72 | 125 | 38.03 | 23.62 | 4.93
GH5SAN54200A | FJ5AN*C42L | 42 | 1575 | 67 | 75 | 46.3 | 35.84 | 2.86
GH5SAN54200A | FJ5AN*C42L | 42 | 1575 | 67 | 85 | 44.29 | 35.02 | 3.17
GH5SAN54200A | FJ5AN*C42L | 42 | 1575 | 67 | 95 | 42.12 | 34.14 | 3.52
GH5SAN54200A | FJ5AN*C42L | 42 | 1575 | 67 | 105 | 39.8 | 33.19 | 3.92
GH5SAN54200A | FJ5AN*C42L | 42 | 1575 | 67 | 115 | 37.33 | 32.18 | 4.38
GH5SAN54200A | FJ5AN*C42L | 42 | 1575 | 67 | 125 | 34.72 | 31.09 | 4.91
GH5SAN54200A | FJ5AN*C42L | 42 | 1575 | 62 | 75 | 43.03 | 42.54 | 2.85
GH5SAN54200A | FJ5AN*C42L | 42 | 1575 | 62 | 85 | 41.35 | 41.35 | 3.16
GH5SAN54200A | FJ5AN*C42L | 42 | 1575 | 62 | 95 | 39.66 | 39.66 | 3.51
GH5SAN54200A | FJ5AN*C42L | 42 | 1575 | 62 | 105 | 37.83 | 37.83 | 3.91
GH5SAN54200A | FJ5AN*C42L | 42 | 1575 | 62 | 115 | 35.84 | 35.84 | 4.37
GH5SAN54200A | FJ5AN*C42L | 42 | 1575 | 62 | 125 | 33.7 | 33.7 | 4.9
GH5SAN54800A | FJ5AN*C48L | 48 | 1250 | 72 | 75 | 56.66 | 28.52 | 3.15
GH5SAN54800A | FJ5AN*C48L | 48 | 1250 | 72 | 85 | 54.39 | 27.64 | 3.52
GH5SAN54800A | FJ5AN*C48L | 48 | 1250 | 72 | 95 | 51.91 | 26.69 | 3.95
GH5SAN54800A | FJ5AN*C48L | 48 | 1250 | 72 | 105 | 49.15 | 25.65 | 4.43
GH5SAN54800A | FJ5AN*C48L | 48 | 1250 | 72 | 115 | 46.05 | 24.49 | 4.98
GH5SAN54800A | FJ5AN*C48L | 48 | 1250 | 72 | 125 | 42.62 | 23.24 | 5.61
GH5SAN54800A | FJ5AN*C48L | 48 | 1250 | 67 | 75 | 51.3 | 34.6 | 3.14
GH5SAN54800A | FJ5AN*C48L | 48 | 1250 | 67 | 85 | 49.27 | 33.73 | 3.5
GH5SAN54800A | FJ5AN*C48L | 48 | 1250 | 67 | 95 | 47 | 32.78 | 3.92
GH5SAN54800A | FJ5AN*C48L | 48 | 1250 | 67 | 105 | 44.48 | 31.73 | 4.4
GH5SAN54800A | FJ5AN*C48L | 48 | 1250 | 67 | 115 | 41.69 | 30.58 | 4.94
GH5SAN54800A | FJ5AN*C48L | 48 | 1250 | 67 | 125 | 38.53 | 29.3 | 5.57
GH5SAN54800A | FJ5AN*C48L | 48 | 1250 | 62 | 75 | 46.66 | 40.62 | 3.13
GH5SAN54800A | FJ5AN*C48L | 48 | 1250 | 62 | 85 | 44.79 | 39.73 | 3.48
GH5SAN54800A | FJ5AN*C48L | 48 | 1250 | 62 | 95 | 42.76 | 38.76 | 3.89
GH5SAN54800A | FJ5AN*C48L | 48 | 1250 | 62 | 105 | 40.51 | 37.68 | 4.37
GH5SAN54800A | FJ5AN*C48L | 48 | 1250 | 62 | 115 | 38.02 | 36.46 | 4.92
GH5SAN54800A | FJ5AN*C48L | 48 | 1250 | 62 | 125 | 35.31 | 35.31 | 5.54
GH5SAN54800A | FJ5AN*C48L | 48 | 1600 | 72 | 75 | 58.89 | 31.23 | 3.24
GH5SAN54800A | FJ5AN*C48L | 48 | 1600 | 72 | 85 | 56.4 | 30.32 | 3.62
GH5SAN54800A | FJ5AN*C48L | 48 | 1600 | 72 | 95 | 53.69 | 29.33 | 4.05
GH5SAN54800A | FJ5AN*C48L | 48 | 1600 | 72 | 105 | 50.71 | 28.26 | 4.54
GH5SAN54800A | FJ5AN*C48L | 48 | 1600 | 72 | 115 | 47.38 | 27.07 | 5.1
GH5SAN54800A | FJ5AN*C48L | 48 | 1600 | 72 | 125 | 43.69 | 25.78 | 5.72
GH5SAN54800A | FJ5AN*C48L | 48 | 1600 | 67 | 75 | 53.41 | 38.98 | 3.23
GH5SAN54800A | FJ5AN*C48L | 48 | 1600 | 67 | 85 | 51.15 | 38.06 | 3.6
GH5SAN54800A | FJ5AN*C48L | 48 | 1600 | 67 | 95 | 48.72 | 37.07 | 4.02
GH5SAN54800A | FJ5AN*C48L | 48 | 1600 | 67 | 105 | 46 | 35.96 | 4.51
GH5SAN54800A | FJ5AN*C48L | 48 | 1600 | 67 | 115 | 43 | 34.78 | 5.05
GH5SAN54800A | FJ5AN*C48L | 48 | 1600 | 67 | 125 | 39.66 | 33.45 | 5.68
GH5SAN54800A | FJ5AN*C48L | 48 | 1600 | 62 | 75 | 48.96 | 46.5 | 3.23
GH5SAN54800A | FJ5AN*C48L | 48 | 1600 | 62 | 85 | 46.99 | 45.48 | 3.58
GH5SAN54800A | FJ5AN*C48L | 48 | 1600 | 62 | 95 | 45.02 | 43.97 | 4
GH5SAN54800A | FJ5AN*C48L | 48 | 1600 | 62 | 105 | 42.79 | 42.79 | 4.48
GH5SAN54800A | FJ5AN*C48L | 48 | 1600 | 62 | 115 | 40.49 | 40.49 | 5.03
GH5SAN54800A | FJ5AN*C48L | 48 | 1600 | 62 | 125 | 37.87 | 37.87 | 5.66
GH5SAN54800A | FJ5AN*C48L | 48 | 1800 | 72 | 75 | 59.74 | 32.68 | 3.3
GH5SAN54800A | FJ5AN*C48L | 48 | 1800 | 72 | 85 | 57.16 | 31.75 | 3.68
GH5SAN54800A | FJ5AN*C48L | 48 | 1800 | 72 | 95 | 54.36 | 30.75 | 4.11
GH5SAN54800A | FJ5AN*C48L | 48 | 1800 | 72 | 105 | 51.26 | 29.65 | 4.6
GH5SAN54800A | FJ5AN*C48L | 48 | 1800 | 72 | 115 | 47.81 | 28.43 | 5.15
GH5SAN54800A | FJ5AN*C48L | 48 | 1800 | 72 | 125 | 44.06 | 27.15 | 5.78
GH5SAN54800A | FJ5AN*C48L | 48 | 1800 | 67 | 75 | 54.23 | 41.34 | 3.29
GH5SAN54800A | FJ5AN*C48L | 48 | 1800 | 67 | 85 | 51.9 | 40.4 | 3.66
GH5SAN54800A | FJ5AN*C48L | 48 | 1800 | 67 | 95 | 49.39 | 39.39 | 4.08
GH5SAN54800A | FJ5AN*C48L | 48 | 1800 | 67 | 105 | 46.6 | 38.27 | 4.56
GH5SAN54800A | FJ5AN*C48L | 48 | 1800 | 67 | 115 | 43.52 | 37.04 | 5.11
GH5SAN54800A | FJ5AN*C48L | 48 | 1800 | 67 | 125 | 40.11 | 35.66 | 5.74
GH5SAN54800A | FJ5AN*C48L | 48 | 1800 | 62 | 75 | 50.1 | 50.1 | 3.28
GH5SAN54800A | FJ5AN*C48L | 48 | 1800 | 62 | 85 | 48.27 | 48.27 | 3.64
GH5SAN54800A | FJ5AN*C48L | 48 | 1800 | 62 | 95 | 46.33 | 46.33 | 4.06
GH5SAN54800A | FJ5AN*C48L | 48 | 1800 | 62 | 105 | 44.16 | 44.16 | 4.54
GH5SAN54800A | FJ5AN*C48L | 48 | 1800 | 62 | 115 | 41.72 | 41.72 | 5.09
GH5SAN54800A | FJ5AN*C48L | 48 | 1800 | 62 | 125 | 38.97 | 38.97 | 5.73
GH5SAN56000A | FJ5AN*D60L | 60 | 1775 | 72 | 75 | 69.13 | 35.84 | 4.07
GH5SAN56000A | FJ5AN*D60L | 60 | 1775 | 72 | 85 | 66.01 | 34.69 | 4.53
GH5SAN56000A | FJ5AN*D60L | 60 | 1775 | 72 | 95 | 62.68 | 33.48 | 5.05
GH5SAN56000A | FJ5AN*D60L | 60 | 1775 | 72 | 105 | 58.98 | 32.15 | 5.64
GH5SAN56000A | FJ5AN*D60L | 60 | 1775 | 72 | 115 | 55.14 | 30.78 | 6.31
GH5SAN56000A | FJ5AN*D60L | 60 | 1775 | 72 | 125 | 50.84 | 29.3 | 7.06
GH5SAN56000A | FJ5AN*D60L | 60 | 1775 | 67 | 75 | 63.31 | 44.81 | 4.03
GH5SAN56000A | FJ5AN*D60L | 60 | 1775 | 67 | 85 | 60.51 | 43.67 | 4.49
GH5SAN56000A | FJ5AN*D60L | 60 | 1775 | 67 | 95 | 57.5 | 42.45 | 5
GH5SAN56000A | FJ5AN*D60L | 60 | 1775 | 67 | 105 | 54.24 | 41.14 | 5.59
GH5SAN56000A | FJ5AN*D60L | 60 | 1775 | 67 | 115 | 50.69 | 39.73 | 6.25
GH5SAN56000A | FJ5AN*D60L | 60 | 1775 | 67 | 125 | 46.83 | 38.21 | 7.01
GH5SAN56000A | FJ5AN*D60L | 60 | 1775 | 62 | 75 | 58.15 | 53.51 | 4.01
GH5SAN56000A | FJ5AN*D60L | 60 | 1775 | 62 | 85 | 55.69 | 52.32 | 4.45
GH5SAN56000A | FJ5AN*D60L | 60 | 1775 | 62 | 95 | 53.05 | 51.01 | 4.96
GH5SAN56000A | FJ5AN*D60L | 60 | 1775 | 62 | 105 | 50.43 | 49.01 | 5.55
GH5SAN56000A | FJ5AN*D60L | 60 | 1775 | 62 | 115 | 47.56 | 47.56 | 6.22
GH5SAN56000A | FJ5AN*D60L | 60 | 1775 | 62 | 125 | 44.54 | 44.54 | 6.98
GH5SAN56000A | FJ5AN*D60L | 60 | 2000 | 72 | 75 | 70.03 | 37.44 | 4.15
GH5SAN56000A | FJ5AN*D60L | 60 | 2000 | 72 | 85 | 66.79 | 36.27 | 4.61
GH5SAN56000A | FJ5AN*D60L | 60 | 2000 | 72 | 95 | 63.34 | 35.04 | 5.13
GH5SAN56000A | FJ5AN*D60L | 60 | 2000 | 72 | 105 | 59.6 | 33.72 | 5.72
GH5SAN56000A | FJ5AN*D60L | 60 | 2000 | 72 | 115 | 55.57 | 32.31 | 6.39
GH5SAN56000A | FJ5AN*D60L | 60 | 2000 | 72 | 125 | 51.18 | 30.8 | 7.14
GH5SAN56000A | FJ5AN*D60L | 60 | 2000 | 67 | 75 | 64.23 | 47.48 | 4.11
GH5SAN56000A | FJ5AN*D60L | 60 | 2000 | 67 | 85 | 61.33 | 46.31 | 4.56
GH5SAN56000A | FJ5AN*D60L | 60 | 2000 | 67 | 95 | 58.21 | 45.07 | 5.08
GH5SAN56000A | FJ5AN*D60L | 60 | 2000 | 67 | 105 | 54.83 | 43.73 | 5.67
GH5SAN56000A | FJ5AN*D60L | 60 | 2000 | 67 | 115 | 51.19 | 42.3 | 6.33
GH5SAN56000A | FJ5AN*D60L | 60 | 2000 | 67 | 125 | 47.24 | 40.74 | 7.09
GH5SAN56000A | FJ5AN*D60L | 60 | 2000 | 62 | 75 | 59.36 | 57.03 | 4.09
GH5SAN56000A | FJ5AN*D60L | 60 | 2000 | 62 | 85 | 56.89 | 56.89 | 4.53
GH5SAN56000A | FJ5AN*D60L | 60 | 2000 | 62 | 95 | 54.43 | 54.43 | 5.05
GH5SAN56000A | FJ5AN*D60L | 60 | 2000 | 62 | 105 | 51.79 | 51.79 | 5.64
GH5SAN56000A | FJ5AN*D60L | 60 | 2000 | 62 | 115 | 48.93 | 48.93 | 6.31
GH5SAN56000A | FJ5AN*D60L | 60 | 2000 | 62 | 125 | 45.73 | 45.73 | 7.07
GH5SAN56000A | FJ5AN*D60L | 60 | 2250 | 72 | 75 | 70.76 | 39.14 | 4.23
GH5SAN56000A | FJ5AN*D60L | 60 | 2250 | 72 | 85 | 67.42 | 37.96 | 4.7
GH5SAN56000A | FJ5AN*D60L | 60 | 2250 | 72 | 95 | 63.84 | 36.71 | 5.22
GH5SAN56000A | FJ5AN*D60L | 60 | 2250 | 72 | 105 | 60 | 35.37 | 5.81
GH5SAN56000A | FJ5AN*D60L | 60 | 2250 | 72 | 115 | 55.87 | 33.96 | 6.48
GH5SAN56000A | FJ5AN*D60L | 60 | 2250 | 72 | 125 | 51.32 | 32.43 | 7.23
GH5SAN56000A | FJ5AN*D60L | 60 | 2250 | 67 | 75 | 64.99 | 50.33 | 4.2
GH5SAN56000A | FJ5AN*D60L | 60 | 2250 | 67 | 85 | 62 | 49.14 | 4.65
GH5SAN56000A | FJ5AN*D60L | 60 | 2250 | 67 | 95 | 58.79 | 47.87 | 5.17
GH5SAN56000A | FJ5AN*D60L | 60 | 2250 | 67 | 105 | 55.33 | 46.5 | 5.76
GH5SAN56000A | FJ5AN*D60L | 60 | 2250 | 67 | 115 | 51.6 | 45.01 | 6.42
GH5SAN56000A | FJ5AN*D60L | 60 | 2250 | 67 | 125 | 47.57 | 43.38 | 7.18
GH5SAN56000A | FJ5AN*D60L | 60 | 2250 | 62 | 75 | 61.03 | 59.18 | 4.18
GH5SAN56000A | FJ5AN*D60L | 60 | 2250 | 62 | 85 | 58.5 | 58.5 | 4.63
GH5SAN56000A | FJ5AN*D60L | 60 | 2250 | 62 | 95 | 55.97 | 55.97 | 5.14
GH5SAN56000A | FJ5AN*D60L | 60 | 2250 | 62 | 105 | 53.2 | 53.2 | 5.73
GH5SAN56000A | FJ5AN*D60L | 60 | 2250 | 62 | 115 | 50.14 | 50.14 | 6.4
GH5SAN56000A | FJ5AN*D60L | 60 | 2250 | 62 | 125 | 46.76 | 46.76 | 7.17

## GH5_Heating
ODU_Model | IDU_Model | Size_Nom | EDB_F | CFM | ODB_F | Cap_Total_kBtu | Cap_Integ_kBtu | Sys_kW
GH5SAN51800A | FJ5AN*A18L | 18 | 65 | 540 | -3 | 6.11 | 5.62 | 3.72
GH5SAN51800A | FJ5AN*A18L | 18 | 65 | 540 | 7 | 7.97 | 7.33 | 3.85
GH5SAN51800A | FJ5AN*A18L | 18 | 65 | 540 | 17 | 10.1 | 9.21 | 4.01
GH5SAN51800A | FJ5AN*A18L | 18 | 65 | 540 | 27 | 11.85 | 10.52 | 4.15
GH5SAN51800A | FJ5AN*A18L | 18 | 65 | 540 | 37 | 15.23 | 13.86 | 4.37
GH5SAN51800A | FJ5AN*A18L | 18 | 65 | 540 | 47 | 17.74 | 17.74 | 4.54
GH5SAN51800A | FJ5AN*A18L | 18 | 65 | 540 | 57 | 20.52 | 20.52 | 4.73
GH5SAN51800A | FJ5AN*A18L | 18 | 65 | 540 | 67 | 23.29 | 23.29 | 4.86
GH5SAN51800A | FJ5AN*A18L | 18 | 65 | 600 | -3 | 6.18 | 5.69 | 3.73
GH5SAN51800A | FJ5AN*A18L | 18 | 65 | 600 | 7 | 8.07 | 7.42 | 3.86
GH5SAN51800A | FJ5AN*A18L | 18 | 65 | 600 | 17 | 10.22 | 9.32 | 4
GH5SAN51800A | FJ5AN*A18L | 18 | 65 | 600 | 27 | 12.63 | 11.22 | 4.16
GH5SAN51800A | FJ5AN*A18L | 18 | 65 | 600 | 37 | 15.36 | 13.97 | 4.33
GH5SAN51800A | FJ5AN*A18L | 18 | 65 | 600 | 47 | 17.92 | 17.92 | 4.48
GH5SAN51800A | FJ5AN*A18L | 18 | 65 | 600 | 57 | 20.75 | 20.75 | 4.63
GH5SAN51800A | FJ5AN*A18L | 18 | 65 | 600 | 67 | 23.46 | 23.46 | 4.75
GH5SAN51800A | FJ5AN*A18L | 18 | 65 | 675 | -3 | 6.28 | 5.78 | 3.77
GH5SAN51800A | FJ5AN*A18L | 18 | 65 | 675 | 7 | 8.18 | 7.52 | 3.89
GH5SAN51800A | FJ5AN*A18L | 18 | 65 | 675 | 17 | 10.34 | 9.43 | 4.02
GH5SAN51800A | FJ5AN*A18L | 18 | 65 | 675 | 27 | 12.78 | 11.35 | 4.16
GH5SAN51800A | FJ5AN*A18L | 18 | 65 | 675 | 37 | 15.5 | 14.1 | 4.3
GH5SAN51800A | FJ5AN*A18L | 18 | 65 | 675 | 47 | 18.09 | 18.09 | 4.43
GH5SAN51800A | FJ5AN*A18L | 18 | 65 | 675 | 57 | 20.87 | 20.87 | 4.55
GH5SAN51800A | FJ5AN*A18L | 18 | 65 | 675 | 67 | 23.61 | 23.61 | 4.66
GH5SAN51800A | FJ5AN*A18L | 18 | 70 | 540 | -3 | 5.8 | 5.34 | 3.85
GH5SAN51800A | FJ5AN*A18L | 18 | 70 | 540 | 7 | 7.69 | 7.06 | 4.01
GH5SAN51800A | FJ5AN*A18L | 18 | 70 | 540 | 17 | 9.81 | 8.95 | 4.18
GH5SAN51800A | FJ5AN*A18L | 18 | 70 | 540 | 27 | 12.17 | 10.81 | 4.37
GH5SAN51800A | FJ5AN*A18L | 18 | 70 | 540 | 37 | 15.02 | 13.66 | 4.58
GH5SAN51800A | FJ5AN*A18L | 18 | 70 | 540 | 47 | 17.5 | 17.5 | 4.76
GH5SAN51800A | FJ5AN*A18L | 18 | 70 | 540 | 57 | 20.21 | 20.21 | 4.95
GH5SAN51800A | FJ5AN*A18L | 18 | 70 | 540 | 67 | 23 | 23 | 5.1
GH5SAN51800A | FJ5AN*A18L | 18 | 70 | 600 | -3 | 5.89 | 5.42 | 3.88
GH5SAN51800A | FJ5AN*A18L | 18 | 70 | 600 | 7 | 7.79 | 7.16 | 4.02
GH5SAN51800A | FJ5AN*A18L | 18 | 70 | 600 | 17 | 9.93 | 9.06 | 4.18
GH5SAN51800A | FJ5AN*A18L | 18 | 70 | 600 | 27 | 12.33 | 10.95 | 4.35
GH5SAN51800A | FJ5AN*A18L | 18 | 70 | 600 | 37 | 15.15 | 13.79 | 4.54
GH5SAN51800A | FJ5AN*A18L | 18 | 70 | 600 | 47 | 17.67 | 17.67 | 4.69
GH5SAN51800A | FJ5AN*A18L | 18 | 70 | 600 | 57 | 20.44 | 20.44 | 4.87
GH5SAN51800A | FJ5AN*A18L | 18 | 70 | 600 | 67 | 23.18 | 23.18 | 4.98
GH5SAN51800A | FJ5AN*A18L | 18 | 70 | 675 | -3 | 5.98 | 5.5 | 3.92
GH5SAN51800A | FJ5AN*A18L | 18 | 70 | 675 | 7 | 7.9 | 7.26 | 4.05
GH5SAN51800A | FJ5AN*A18L | 18 | 70 | 675 | 17 | 10.06 | 9.18 | 4.19
GH5SAN51800A | FJ5AN*A18L | 18 | 70 | 675 | 27 | 12.47 | 11.07 | 4.34
GH5SAN51800A | FJ5AN*A18L | 18 | 70 | 675 | 37 | 15.29 | 13.92 | 4.51
GH5SAN51800A | FJ5AN*A18L | 18 | 70 | 675 | 47 | 17.84 | 17.84 | 4.64
GH5SAN51800A | FJ5AN*A18L | 18 | 70 | 675 | 57 | 20.64 | 20.64 | 4.78
GH5SAN51800A | FJ5AN*A18L | 18 | 70 | 675 | 67 | 23.33 | 23.33 | 4.89
GH5SAN51800A | FJ5AN*A18L | 18 | 75 | 540 | -3 | 5.49 | 5.05 | 4
GH5SAN51800A | FJ5AN*A18L | 18 | 75 | 540 | 7 | 7.42 | 6.82 | 4.18
GH5SAN51800A | FJ5AN*A18L | 18 | 75 | 540 | 17 | 9.51 | 8.67 | 4.36
GH5SAN51800A | FJ5AN*A18L | 18 | 75 | 540 | 27 | 11.9 | 10.57 | 4.56
GH5SAN51800A | FJ5AN*A18L | 18 | 75 | 540 | 37 | 14.77 | 13.44 | 4.79
GH5SAN51800A | FJ5AN*A18L | 18 | 75 | 540 | 47 | 17.25 | 17.25 | 4.98
GH5SAN51800A | FJ5AN*A18L | 18 | 75 | 540 | 57 | 19.92 | 19.92 | 5.18
GH5SAN51800A | FJ5AN*A18L | 18 | 75 | 540 | 67 | 22.69 | 22.69 | 5.34
GH5SAN51800A | FJ5AN*A18L | 18 | 75 | 600 | -3 | 5.57 | 5.13 | 4.03
GH5SAN51800A | FJ5AN*A18L | 18 | 75 | 600 | 7 | 7.48 | 6.88 | 4.19
GH5SAN51800A | FJ5AN*A18L | 18 | 75 | 600 | 17 | 9.63 | 8.78 | 4.36
GH5SAN51800A | FJ5AN*A18L | 18 | 75 | 600 | 27 | 12.01 | 10.67 | 4.54
GH5SAN51800A | FJ5AN*A18L | 18 | 75 | 600 | 37 | 14.92 | 13.58 | 4.75
GH5SAN51800A | FJ5AN*A18L | 18 | 75 | 600 | 47 | 17.42 | 17.42 | 4.91
GH5SAN51800A | FJ5AN*A18L | 18 | 75 | 600 | 57 | 20.13 | 20.13 | 5.1
GH5SAN51800A | FJ5AN*A18L | 18 | 75 | 600 | 67 | 22.88 | 22.88 | 5.22
GH5SAN51800A | FJ5AN*A18L | 18 | 75 | 675 | -3 | 5.67 | 5.21 | 4.07
GH5SAN51800A | FJ5AN*A18L | 18 | 75 | 675 | 7 | 7.59 | 6.98 | 4.21
GH5SAN51800A | FJ5AN*A18L | 18 | 75 | 675 | 17 | 9.76 | 8.9 | 4.37
GH5SAN51800A | FJ5AN*A18L | 18 | 75 | 675 | 27 | 12.17 | 10.81 | 4.54
GH5SAN51800A | FJ5AN*A18L | 18 | 75 | 675 | 37 | 15.07 | 13.72 | 4.72
GH5SAN51800A | FJ5AN*A18L | 18 | 75 | 675 | 47 | 17.59 | 17.59 | 4.86
GH5SAN51800A | FJ5AN*A18L | 18 | 75 | 675 | 57 | 20.35 | 20.35 | 5.02
GH5SAN51800A | FJ5AN*A18L | 18 | 75 | 675 | 67 | 23.04 | 23.04 | 5.12
GH5SAN53600A | FJ5AN*B36L | 36 | 65 | 1050 | -3 | 14.05 | 12.93 | 7.41
GH5SAN53600A | FJ5AN*B36L | 36 | 65 | 1050 | 7 | 17.66 | 16.22 | 7.6
GH5SAN53600A | FJ5AN*B36L | 36 | 65 | 1050 | 17 | 22.24 | 20.28 | 7.94
GH5SAN53600A | FJ5AN*B36L | 36 | 65 | 1050 | 27 | 26.39 | 23.44 | 8.26
GH5SAN53600A | FJ5AN*B36L | 36 | 65 | 1050 | 37 | 31.03 | 28.24 | 8.63
GH5SAN53600A | FJ5AN*B36L | 36 | 65 | 1050 | 47 | 36.16 | 36.16 | 9.07
GH5SAN53600A | FJ5AN*B36L | 36 | 65 | 1050 | 57 | 41.82 | 41.82 | 9.56
GH5SAN53600A | FJ5AN*B36L | 36 | 65 | 1050 | 67 | 47.97 | 47.97 | 9.97
GH5SAN53600A | FJ5AN*B36L | 36 | 65 | 1200 | -3 | 14.3 | 13.15 | 7.51
GH5SAN53600A | FJ5AN*B36L | 36 | 65 | 1200 | 7 | 17.93 | 16.48 | 7.66
GH5SAN53600A | FJ5AN*B36L | 36 | 65 | 1200 | 17 | 22.51 | 20.53 | 7.96
GH5SAN53600A | FJ5AN*B36L | 36 | 65 | 1200 | 27 | 26.69 | 23.71 | 8.24
GH5SAN53600A | FJ5AN*B36L | 36 | 65 | 1200 | 37 | 31.41 | 28.58 | 8.58
GH5SAN53600A | FJ5AN*B36L | 36 | 65 | 1200 | 47 | 36.64 | 36.64 | 8.98
GH5SAN53600A | FJ5AN*B36L | 36 | 65 | 1200 | 57 | 42.46 | 42.46 | 9.45
GH5SAN53600A | FJ5AN*B36L | 36 | 65 | 1200 | 67 | 48.35 | 48.35 | 9.79
GH5SAN53600A | FJ5AN*B36L | 36 | 65 | 1350 | -3 | 14.52 | 13.36 | 7.61
GH5SAN53600A | FJ5AN*B36L | 36 | 65 | 1350 | 7 | 18.18 | 16.7 | 7.74
GH5SAN53600A | FJ5AN*B36L | 36 | 65 | 1350 | 17 | 22.75 | 20.74 | 8.01
GH5SAN53600A | FJ5AN*B36L | 36 | 65 | 1350 | 27 | 26.96 | 23.94 | 8.26
GH5SAN53600A | FJ5AN*B36L | 36 | 65 | 1350 | 37 | 31.73 | 28.88 | 8.57
GH5SAN53600A | FJ5AN*B36L | 36 | 65 | 1350 | 47 | 37.05 | 37.05 | 8.95
GH5SAN53600A | FJ5AN*B36L | 36 | 65 | 1350 | 57 | 42.96 | 42.96 | 9.4
GH5SAN53600A | FJ5AN*B36L | 36 | 65 | 1350 | 67 | 48.53 | 48.53 | 9.7
GH5SAN53600A | FJ5AN*B36L | 36 | 70 | 1050 | -3 | 13.52 | 12.43 | 7.67
GH5SAN53600A | FJ5AN*B36L | 36 | 70 | 1050 | 7 | 17.15 | 15.76 | 7.89
GH5SAN53600A | FJ5AN*B36L | 36 | 70 | 1050 | 17 | 21.36 | 19.48 | 8.22
GH5SAN53600A | FJ5AN*B36L | 36 | 70 | 1050 | 27 | 26.02 | 23.11 | 8.63
GH5SAN53600A | FJ5AN*B36L | 36 | 70 | 1050 | 37 | 30.57 | 27.82 | 9.02
GH5SAN53600A | FJ5AN*B36L | 36 | 70 | 1050 | 47 | 35.6 | 35.6 | 9.47
GH5SAN53600A | FJ5AN*B36L | 36 | 70 | 1050 | 57 | 41.11 | 41.11 | 9.96
GH5SAN53600A | FJ5AN*B36L | 36 | 70 | 1050 | 67 | 47.23 | 47.23 | 10.41
GH5SAN53600A | FJ5AN*B36L | 36 | 70 | 1200 | -3 | 13.77 | 12.67 | 7.76
GH5SAN53600A | FJ5AN*B36L | 36 | 70 | 1200 | 7 | 17.43 | 16.02 | 7.96
GH5SAN53600A | FJ5AN*B36L | 36 | 70 | 1200 | 17 | 21.8 | 19.88 | 8.26
GH5SAN53600A | FJ5AN*B36L | 36 | 70 | 1200 | 27 | 26.32 | 23.38 | 8.61
GH5SAN53600A | FJ5AN*B36L | 36 | 70 | 1200 | 37 | 30.95 | 28.16 | 8.97
GH5SAN53600A | FJ5AN*B36L | 36 | 70 | 1200 | 47 | 36.08 | 36.08 | 9.37
GH5SAN53600A | FJ5AN*B36L | 36 | 70 | 1200 | 57 | 41.73 | 41.73 | 9.83
GH5SAN53600A | FJ5AN*B36L | 36 | 70 | 1200 | 67 | 47.7 | 47.7 | 10.19
GH5SAN53600A | FJ5AN*B36L | 36 | 70 | 1350 | -3 | 13.99 | 12.87 | 7.87
GH5SAN53600A | FJ5AN*B36L | 36 | 70 | 1350 | 7 | 17.68 | 16.25 | 8.04
GH5SAN53600A | FJ5AN*B36L | 36 | 70 | 1350 | 17 | 22.39 | 20.41 | 8.36
GH5SAN53600A | FJ5AN*B36L | 36 | 70 | 1350 | 27 | 26.59 | 23.61 | 8.63
GH5SAN53600A | FJ5AN*B36L | 36 | 70 | 1350 | 37 | 31.27 | 28.46 | 8.96
GH5SAN53600A | FJ5AN*B36L | 36 | 70 | 1350 | 47 | 36.48 | 36.48 | 9.34
GH5SAN53600A | FJ5AN*B36L | 36 | 70 | 1350 | 57 | 42.24 | 42.24 | 9.79
GH5SAN53600A | FJ5AN*B36L | 36 | 70 | 1350 | 67 | 47.92 | 47.92 | 10.09
GH5SAN53600A | FJ5AN*B36L | 36 | 75 | 1050 | -3 | 12.93 | 11.9 | 7.93
GH5SAN53600A | FJ5AN*B36L | 36 | 75 | 1050 | 7 | 16.6 | 15.25 | 8.2
GH5SAN53600A | FJ5AN*B36L | 36 | 75 | 1050 | 17 | 20.77 | 18.94 | 8.56
GH5SAN53600A | FJ5AN*B36L | 36 | 75 | 1050 | 27 | 25.64 | 22.77 | 9.03
GH5SAN53600A | FJ5AN*B36L | 36 | 75 | 1050 | 37 | 30.11 | 27.4 | 9.44
GH5SAN53600A | FJ5AN*B36L | 36 | 75 | 1050 | 47 | 35.04 | 35.04 | 9.89
GH5SAN53600A | FJ5AN*B36L | 36 | 75 | 1050 | 57 | 40.45 | 40.45 | 10.38
GH5SAN53600A | FJ5AN*B36L | 36 | 75 | 1050 | 67 | 46.44 | 46.44 | 10.88
GH5SAN53600A | FJ5AN*B36L | 36 | 75 | 1200 | -3 | 13.18 | 12.13 | 8.02
GH5SAN53600A | FJ5AN*B36L | 36 | 75 | 1200 | 7 | 16.88 | 15.51 | 8.27
GH5SAN53600A | FJ5AN*B36L | 36 | 75 | 1200 | 17 | 21.11 | 19.24 | 8.58
GH5SAN53600A | FJ5AN*B36L | 36 | 75 | 1200 | 27 | 25.94 | 23.04 | 9
GH5SAN53600A | FJ5AN*B36L | 36 | 75 | 1200 | 37 | 30.48 | 27.74 | 9.37
GH5SAN53600A | FJ5AN*B36L | 36 | 75 | 1200 | 47 | 35.51 | 35.51 | 9.78
GH5SAN53600A | FJ5AN*B36L | 36 | 75 | 1200 | 57 | 41.03 | 41.03 | 10.24
GH5SAN53600A | FJ5AN*B36L | 36 | 75 | 1200 | 67 | 47.01 | 47.01 | 10.62
GH5SAN53600A | FJ5AN*B36L | 36 | 75 | 1350 | -3 | 13.41 | 12.34 | 8.13
GH5SAN53600A | FJ5AN*B36L | 36 | 75 | 1350 | 7 | 17.13 | 15.75 | 8.35
GH5SAN53600A | FJ5AN*B36L | 36 | 75 | 1350 | 17 | 21.4 | 19.51 | 8.64
GH5SAN53600A | FJ5AN*B36L | 36 | 75 | 1350 | 27 | 26.2 | 23.27 | 9.02
GH5SAN53600A | FJ5AN*B36L | 36 | 75 | 1350 | 37 | 30.8 | 28.03 | 9.36
GH5SAN53600A | FJ5AN*B36L | 36 | 75 | 1350 | 47 | 35.9 | 35.9 | 9.74
GH5SAN53600A | FJ5AN*B36L | 36 | 75 | 1350 | 57 | 41.51 | 41.51 | 10.19
GH5SAN53600A | FJ5AN*B36L | 36 | 75 | 1350 | 67 | 47.29 | 47.29 | 10.5
GH5SAN54800A | FJ5AN*C48L | 48 | 65 | 1250 | -3 | 17.68 | 16.27 | 9.65
GH5SAN54800A | FJ5AN*C48L | 48 | 65 | 1250 | 7 | 22.95 | 21.09 | 10.11
GH5SAN54800A | FJ5AN*C48L | 48 | 65 | 1250 | 17 | 28.59 | 26.07 | 10.57
GH5SAN54800A | FJ5AN*C48L | 48 | 65 | 1250 | 27 | 34.91 | 31 | 11.08
GH5SAN54800A | FJ5AN*C48L | 48 | 65 | 1250 | 37 | 41.53 | 37.79 | 11.64
GH5SAN54800A | FJ5AN*C48L | 48 | 65 | 1250 | 47 | 48.12 | 48.12 | 12.17
GH5SAN54800A | FJ5AN*C48L | 48 | 65 | 1250 | 57 | 55.75 | 55.75 | 12.87
GH5SAN54800A | FJ5AN*C48L | 48 | 65 | 1250 | 67 | 64.5 | 64.5 | 13.78
GH5SAN54800A | FJ5AN*C48L | 48 | 65 | 1600 | -3 | 18.33 | 16.86 | 9.76
GH5SAN54800A | FJ5AN*C48L | 48 | 65 | 1600 | 7 | 23.68 | 21.76 | 10.15
GH5SAN54800A | FJ5AN*C48L | 48 | 65 | 1600 | 17 | 29.41 | 26.82 | 10.52
GH5SAN54800A | FJ5AN*C48L | 48 | 65 | 1600 | 27 | 36.3 | 32.24 | 11
GH5SAN54800A | FJ5AN*C48L | 48 | 65 | 1600 | 37 | 42.36 | 38.55 | 11.34
GH5SAN54800A | FJ5AN*C48L | 48 | 65 | 1600 | 47 | 49.2 | 49.2 | 11.74
GH5SAN54800A | FJ5AN*C48L | 48 | 65 | 1600 | 57 | 57.22 | 57.22 | 12.27
GH5SAN54800A | FJ5AN*C48L | 48 | 65 | 1600 | 67 | 66.5 | 66.5 | 12.99
GH5SAN54800A | FJ5AN*C48L | 48 | 65 | 1800 | -3 | 18.63 | 17.14 | 9.86
GH5SAN54800A | FJ5AN*C48L | 48 | 65 | 1800 | 7 | 24.01 | 22.06 | 10.22
GH5SAN54800A | FJ5AN*C48L | 48 | 65 | 1800 | 17 | 29.78 | 27.16 | 10.56
GH5SAN54800A | FJ5AN*C48L | 48 | 65 | 1800 | 27 | 36.61 | 32.52 | 10.99
GH5SAN54800A | FJ5AN*C48L | 48 | 65 | 1800 | 37 | 42.73 | 38.88 | 11.29
GH5SAN54800A | FJ5AN*C48L | 48 | 65 | 1800 | 47 | 49.67 | 49.67 | 11.64
GH5SAN54800A | FJ5AN*C48L | 48 | 65 | 1800 | 57 | 57.82 | 57.82 | 12.11
GH5SAN54800A | FJ5AN*C48L | 48 | 65 | 1800 | 67 | 67.24 | 67.24 | 12.74
GH5SAN54800A | FJ5AN*C48L | 48 | 70 | 1250 | -3 | 16.72 | 15.38 | 10.06
GH5SAN54800A | FJ5AN*C48L | 48 | 70 | 1250 | 7 | 22.16 | 20.36 | 10.56
GH5SAN54800A | FJ5AN*C48L | 48 | 70 | 1250 | 17 | 27.86 | 25.4 | 11.04
GH5SAN54800A | FJ5AN*C48L | 48 | 70 | 1250 | 27 | 34.08 | 30.27 | 11.57
GH5SAN54800A | FJ5AN*C48L | 48 | 70 | 1250 | 37 | 41.05 | 37.36 | 12.21
GH5SAN54800A | FJ5AN*C48L | 48 | 70 | 1250 | 47 | 47.5 | 47.5 | 12.77
GH5SAN54800A | FJ5AN*C48L | 48 | 70 | 1250 | 57 | 54.97 | 54.97 | 13.49
GH5SAN54800A | FJ5AN*C48L | 48 | 70 | 1250 | 67 | 63.5 | 63.5 | 14.43
GH5SAN54800A | FJ5AN*C48L | 48 | 70 | 1600 | -3 | 17.42 | 16.02 | 10.18
GH5SAN54800A | FJ5AN*C48L | 48 | 70 | 1600 | 7 | 22.81 | 20.96 | 10.58
GH5SAN54800A | FJ5AN*C48L | 48 | 70 | 1600 | 17 | 28.65 | 26.12 | 10.98
GH5SAN54800A | FJ5AN*C48L | 48 | 70 | 1600 | 27 | 34.98 | 31.06 | 11.39
GH5SAN54800A | FJ5AN*C48L | 48 | 70 | 1600 | 37 | 41.85 | 38.08 | 11.88
GH5SAN54800A | FJ5AN*C48L | 48 | 70 | 1600 | 47 | 48.56 | 48.56 | 12.3
GH5SAN54800A | FJ5AN*C48L | 48 | 70 | 1600 | 57 | 56.41 | 56.41 | 12.86
GH5SAN54800A | FJ5AN*C48L | 48 | 70 | 1600 | 67 | 65.49 | 65.49 | 13.61
GH5SAN54800A | FJ5AN*C48L | 48 | 70 | 1800 | -3 | 17.61 | 16.2 | 10.27
GH5SAN54800A | FJ5AN*C48L | 48 | 70 | 1800 | 7 | 23.19 | 21.31 | 10.65
GH5SAN54800A | FJ5AN*C48L | 48 | 70 | 1800 | 17 | 29.01 | 26.45 | 11.01
GH5SAN54800A | FJ5AN*C48L | 48 | 70 | 1800 | 27 | 35.48 | 31.51 | 11.39
GH5SAN54800A | FJ5AN*C48L | 48 | 70 | 1800 | 37 | 42.22 | 38.42 | 11.81
GH5SAN54800A | FJ5AN*C48L | 48 | 70 | 1800 | 47 | 49.02 | 49.02 | 12.19
GH5SAN54800A | FJ5AN*C48L | 48 | 70 | 1800 | 57 | 57.01 | 57.01 | 12.69
GH5SAN54800A | FJ5AN*C48L | 48 | 70 | 1800 | 67 | 66.28 | 66.28 | 13.38
GH5SAN54800A | FJ5AN*C48L | 48 | 75 | 1250 | -3 | 15.9 | 14.63 | 10.52
GH5SAN54800A | FJ5AN*C48L | 48 | 75 | 1250 | 7 | 21.27 | 19.55 | 11.04
GH5SAN54800A | FJ5AN*C48L | 48 | 75 | 1250 | 17 | 27.07 | 24.68 | 11.54
GH5SAN54800A | FJ5AN*C48L | 48 | 75 | 1250 | 27 | 33.36 | 29.63 | 12.12
GH5SAN54800A | FJ5AN*C48L | 48 | 75 | 1250 | 37 | 40.57 | 36.92 | 12.83
GH5SAN54800A | FJ5AN*C48L | 48 | 75 | 1250 | 47 | 46.89 | 46.89 | 13.4
GH5SAN54800A | FJ5AN*C48L | 48 | 75 | 1250 | 57 | 54.17 | 54.17 | 14.15
GH5SAN54800A | FJ5AN*C48L | 48 | 75 | 1250 | 67 | 62.5 | 62.5 | 15.11
GH5SAN54800A | FJ5AN*C48L | 48 | 75 | 1600 | -3 | 16.5 | 15.18 | 10.63
GH5SAN54800A | FJ5AN*C48L | 48 | 75 | 1600 | 7 | 22.04 | 20.25 | 11.06
GH5SAN54800A | FJ5AN*C48L | 48 | 75 | 1600 | 17 | 27.89 | 25.43 | 11.47
GH5SAN54800A | FJ5AN*C48L | 48 | 75 | 1600 | 27 | 34.21 | 30.38 | 11.91
GH5SAN54800A | FJ5AN*C48L | 48 | 75 | 1600 | 37 | 41.36 | 37.63 | 12.46
GH5SAN54800A | FJ5AN*C48L | 48 | 75 | 1600 | 47 | 47.93 | 47.93 | 12.9
GH5SAN54800A | FJ5AN*C48L | 48 | 75 | 1600 | 57 | 55.6 | 55.6 | 13.48
GH5SAN54800A | FJ5AN*C48L | 48 | 75 | 1600 | 67 | 64.47 | 64.47 | 14.26
GH5SAN54800A | FJ5AN*C48L | 48 | 75 | 1800 | -3 | 16.78 | 15.43 | 10.73
GH5SAN54800A | FJ5AN*C48L | 48 | 75 | 1800 | 7 | 22.36 | 20.54 | 11.12
GH5SAN54800A | FJ5AN*C48L | 48 | 75 | 1800 | 17 | 28.23 | 25.74 | 11.5
GH5SAN54800A | FJ5AN*C48L | 48 | 75 | 1800 | 27 | 34.58 | 30.71 | 11.89
GH5SAN54800A | FJ5AN*C48L | 48 | 75 | 1800 | 37 | 41.7 | 37.95 | 12.38
GH5SAN54800A | FJ5AN*C48L | 48 | 75 | 1800 | 47 | 48.38 | 48.38 | 12.78
GH5SAN54800A | FJ5AN*C48L | 48 | 75 | 1800 | 57 | 56.2 | 56.2 | 13.3
GH5SAN54800A | FJ5AN*C48L | 48 | 75 | 1800 | 67 | 65.25 | 65.25 | 14.01

## GH8_Detail_Cool
ODU_Model | IDU_Model | Size_Nom | CFM | EWB_F | ODB_F | TC_Net_kBtu | Sens_Net_kBtu | Sys_kW | Stage
GH8TAN52400A | FG5ANXB24L | 24 | 650 | 72 | 75 | 27.51 | 14.01 | 1.36 | High
GH8TAN52400A | FG5ANXB24L | 24 | 650 | 72 | 85 | 26.38 | 13.58 | 1.55 | High
GH8TAN52400A | FG5ANXB24L | 24 | 650 | 72 | 95 | 25.14 | 13.11 | 1.75 | High
GH8TAN52400A | FG5ANXB24L | 24 | 650 | 72 | 105 | 23.78 | 12.61 | 1.97 | High
GH8TAN52400A | FG5ANXB24L | 24 | 650 | 67 | 75 | 24.86 | 17.13 | 1.37 | High
GH8TAN52400A | FG5ANXB24L | 24 | 650 | 67 | 85 | 23.84 | 16.7 | 1.56 | High
GH8TAN52400A | FG5ANXB24L | 24 | 650 | 67 | 95 | 22.71 | 16.21 | 1.75 | High
GH8TAN52400A | FG5ANXB24L | 24 | 650 | 67 | 105 | 21.47 | 15.72 | 1.97 | High
GH8TAN52400A | FG5ANXB24L | 24 | 650 | 62 | 75 | 22.58 | 20.2 | 1.39 | High
GH8TAN52400A | FG5ANXB24L | 24 | 650 | 62 | 85 | 21.64 | 19.75 | 1.56 | High
GH8TAN52400A | FG5ANXB24L | 24 | 650 | 62 | 95 | 20.62 | 19.27 | 1.75 | High
GH8TAN52400A | FG5ANXB24L | 24 | 650 | 62 | 105 | 19.53 | 18.74 | 1.97 | High
GH8TAN52400A | FG5ANXB24L | 24 | 700 | 72 | 75 | 27.85 | 14.41 | 1.37 | High
GH8TAN52400A | FG5ANXB24L | 24 | 700 | 72 | 85 | 26.69 | 13.97 | 1.56 | High
GH8TAN52400A | FG5ANXB24L | 24 | 700 | 72 | 95 | 25.41 | 13.49 | 1.76 | High
GH8TAN52400A | FG5ANXB24L | 24 | 700 | 72 | 105 | 24.02 | 12.98 | 1.99 | High
GH8TAN52400A | FG5ANXB24L | 24 | 700 | 67 | 75 | 25.18 | 17.76 | 1.39 | High
GH8TAN52400A | FG5ANXB24L | 24 | 700 | 67 | 85 | 24.11 | 17.31 | 1.57 | High
GH8TAN52400A | FG5ANXB24L | 24 | 700 | 67 | 95 | 22.97 | 16.84 | 1.77 | High
GH8TAN52400A | FG5ANXB24L | 24 | 700 | 67 | 105 | 21.7 | 16.33 | 1.99 | High
GH8TAN52400A | FG5ANXB24L | 24 | 700 | 62 | 75 | 22.91 | 21.06 | 1.4 | High
GH8TAN52400A | FG5ANXB24L | 24 | 700 | 62 | 85 | 21.95 | 20.6 | 1.58 | High
GH8TAN52400A | FG5ANXB24L | 24 | 700 | 62 | 95 | 20.91 | 20.09 | 1.77 | High
GH8TAN52400A | FG5ANXB24L | 24 | 700 | 62 | 105 | 19.83 | 19.48 | 1.98 | High
GH8TAN52400A | FG5ANXB24L | 24 | 805 | 72 | 75 | 28.41 | 15.2 | 1.4 | High
GH8TAN52400A | FG5ANXB24L | 24 | 805 | 72 | 85 | 27.19 | 14.75 | 1.59 | High
GH8TAN52400A | FG5ANXB24L | 24 | 805 | 72 | 95 | 25.86 | 14.26 | 1.8 | High
GH8TAN52400A | FG5ANXB24L | 24 | 805 | 72 | 105 | 24.4 | 13.74 | 2.02 | High
GH8TAN52400A | FG5ANXB24L | 24 | 805 | 67 | 75 | 25.71 | 19.04 | 1.42 | High
GH8TAN52400A | FG5ANXB24L | 24 | 805 | 67 | 85 | 24.6 | 18.59 | 1.6 | High
GH8TAN52400A | FG5ANXB24L | 24 | 805 | 67 | 95 | 23.4 | 18.1 | 1.8 | High
GH8TAN52400A | FG5ANXB24L | 24 | 805 | 67 | 105 | 22.08 | 17.58 | 2.02 | High
GH8TAN52400A | FG5ANXB24L | 24 | 805 | 62 | 75 | 23.53 | 22.76 | 1.43 | High
GH8TAN52400A | FG5ANXB24L | 24 | 805 | 62 | 85 | 22.57 | 22.23 | 1.61 | High
GH8TAN52400A | FG5ANXB24L | 24 | 805 | 62 | 95 | 21.77 | 21.02 | 1.8 | High
GH8TAN52400A | FG5ANXB24L | 24 | 805 | 62 | 105 | 20.59 | 20.59 | 2.02 | High
GH8TAN52400A | FG5ANXB24L | 24 | 480 | 72 | 75 | 20.1 | 10.36 | 0.84 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 480 | 72 | 85 | 19.29 | 10.08 | 0.97 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 480 | 72 | 95 | 18.41 | 9.77 | 1.1 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 480 | 72 | 105 | 17.44 | 9.43 | 1.24 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 480 | 67 | 75 | 18.08 | 12.67 | 0.87 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 480 | 67 | 85 | 17.36 | 12.41 | 0.99 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 480 | 67 | 95 | 16.54 | 12.11 | 1.12 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 480 | 67 | 105 | 15.67 | 11.8 | 1.26 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 480 | 62 | 75 | 16.32 | 14.91 | 0.89 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 480 | 62 | 85 | 15.69 | 14.67 | 1.01 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 480 | 62 | 95 | 14.98 | 14.39 | 1.14 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 480 | 62 | 105 | 14.21 | 14.09 | 1.28 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 560 | 72 | 75 | 20.62 | 11.03 | 0.85 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 560 | 72 | 85 | 19.75 | 10.73 | 0.98 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 560 | 72 | 95 | 18.81 | 10.42 | 1.11 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 560 | 72 | 105 | 17.78 | 10.08 | 1.25 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 560 | 67 | 75 | 18.58 | 13.71 | 0.88 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 560 | 67 | 85 | 17.8 | 13.45 | 1 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 560 | 67 | 95 | 16.96 | 13.17 | 1.13 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 560 | 67 | 105 | 16.03 | 12.82 | 1.27 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 560 | 62 | 75 | 16.86 | 16.32 | 0.9 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 560 | 62 | 85 | 16.3 | 15.83 | 1.02 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 560 | 62 | 95 | 15.58 | 15.58 | 1.15 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 560 | 62 | 105 | 14.87 | 14.87 | 1.28 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 645 | 72 | 75 | 21.02 | 11.72 | 0.86 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 645 | 72 | 85 | 20.11 | 11.42 | 0.99 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 645 | 72 | 95 | 19.14 | 11.04 | 1.12 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 645 | 72 | 105 | 18.04 | 10.74 | 1.26 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 645 | 67 | 75 | 18.96 | 14.79 | 0.89 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 645 | 67 | 85 | 18.16 | 14.52 | 1.01 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 645 | 67 | 95 | 17.27 | 14.22 | 1.14 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 645 | 67 | 105 | 16.3 | 13.9 | 1.28 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 645 | 62 | 75 | 17.48 | 17.48 | 0.91 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 645 | 62 | 85 | 16.91 | 16.91 | 1.03 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 645 | 62 | 95 | 16.27 | 16.27 | 1.16 | Low
GH8TAN52400A | FG5ANXB24L | 24 | 645 | 62 | 105 | 15.55 | 15.55 | 1.29 | Low
GH8TAN53600A | FG5ANXC36L | 36 | 975 | 72 | 75 | 40.51 | 20.53 | 2.32 | High
GH8TAN53600A | FG5ANXC36L | 36 | 975 | 72 | 85 | 38.91 | 19.91 | 2.55 | High
GH8TAN53600A | FG5ANXC36L | 36 | 975 | 72 | 95 | 37.22 | 19.27 | 2.81 | High
GH8TAN53600A | FG5ANXC36L | 36 | 975 | 72 | 105 | 35.37 | 18.57 | 3.12 | High
GH8TAN53600A | FG5ANXC36L | 36 | 975 | 67 | 75 | 36.67 | 25.1 | 2.31 | High
GH8TAN53600A | FG5ANXC36L | 36 | 975 | 67 | 85 | 35.18 | 24.47 | 2.54 | High
GH8TAN53600A | FG5ANXC36L | 36 | 975 | 67 | 95 | 33.62 | 23.82 | 2.81 | High
GH8TAN53600A | FG5ANXC36L | 36 | 975 | 67 | 105 | 31.96 | 23.13 | 3.11 | High
GH8TAN53600A | FG5ANXC36L | 36 | 975 | 62 | 75 | 33.41 | 29.62 | 2.3 | High
GH8TAN53600A | FG5ANXC36L | 36 | 975 | 62 | 85 | 32.07 | 28.97 | 2.53 | High
GH8TAN53600A | FG5ANXC36L | 36 | 975 | 62 | 95 | 30.67 | 28.29 | 2.8 | High
GH8TAN53600A | FG5ANXC36L | 36 | 975 | 62 | 105 | 29.18 | 27.55 | 3.11 | High
GH8TAN53600A | FG5ANXC36L | 36 | 1050 | 72 | 75 | 40.99 | 21.07 | 2.35 | High
GH8TAN53600A | FG5ANXC36L | 36 | 1050 | 72 | 85 | 39.34 | 20.45 | 2.58 | High
GH8TAN53600A | FG5ANXC36L | 36 | 1050 | 72 | 95 | 37.6 | 19.8 | 2.84 | High
GH8TAN53600A | FG5ANXC36L | 36 | 1050 | 72 | 105 | 35.74 | 19.11 | 3.15 | High
GH8TAN53600A | FG5ANXC36L | 36 | 1050 | 67 | 75 | 37.1 | 25.97 | 2.34 | High
GH8TAN53600A | FG5ANXC36L | 36 | 1050 | 67 | 85 | 35.6 | 25.35 | 2.57 | High
GH8TAN53600A | FG5ANXC36L | 36 | 1050 | 67 | 95 | 34 | 24.69 | 2.83 | High
GH8TAN53600A | FG5ANXC36L | 36 | 1050 | 67 | 105 | 32.29 | 23.99 | 3.14 | High
GH8TAN53600A | FG5ANXC36L | 36 | 1050 | 62 | 75 | 33.87 | 30.8 | 2.32 | High
GH8TAN53600A | FG5ANXC36L | 36 | 1050 | 62 | 85 | 32.51 | 30.13 | 2.56 | High
GH8TAN53600A | FG5ANXC36L | 36 | 1050 | 62 | 95 | 31.09 | 29.42 | 2.82 | High
GH8TAN53600A | FG5ANXC36L | 36 | 1050 | 62 | 105 | 29.6 | 28.64 | 3.13 | High
GH8TAN53600A | FG5ANXC36L | 36 | 1205 | 72 | 75 | 41.76 | 22.13 | 2.4 | High
GH8TAN53600A | FG5ANXC36L | 36 | 1205 | 72 | 85 | 40.04 | 21.5 | 2.63 | High
GH8TAN53600A | FG5ANXC36L | 36 | 1205 | 72 | 95 | 38.23 | 20.84 | 2.89 | High
GH8TAN53600A | FG5ANXC36L | 36 | 1205 | 72 | 105 | 36.29 | 20.14 | 3.2 | High
GH8TAN53600A | FG5ANXC36L | 36 | 1205 | 67 | 75 | 37.81 | 27.71 | 2.39 | High
GH8TAN53600A | FG5ANXC36L | 36 | 1205 | 67 | 85 | 36.26 | 27.08 | 2.62 | High
GH8TAN53600A | FG5ANXC36L | 36 | 1205 | 67 | 95 | 34.6 | 26.4 | 2.88 | High
GH8TAN53600A | FG5ANXC36L | 36 | 1205 | 67 | 105 | 32.83 | 25.68 | 3.19 | High
GH8TAN53600A | FG5ANXC36L | 36 | 1205 | 62 | 75 | 34.73 | 33.07 | 2.38 | High
GH8TAN53600A | FG5ANXC36L | 36 | 1205 | 62 | 85 | 33.35 | 32.32 | 2.61 | High
GH8TAN53600A | FG5ANXC36L | 36 | 1205 | 62 | 95 | 32.3 | 30.52 | 2.88 | High
GH8TAN53600A | FG5ANXC36L | 36 | 1205 | 62 | 105 | 30.54 | 30.54 | 3.19 | High
GH8TAN54800A | FG5ANBD60L | 48 | 1400 | 72 | 75 | 58 | 28.76 | 2.96 | High
GH8TAN54800A | FG5ANBD60L | 48 | 1400 | 72 | 85 | 55.53 | 27.93 | 3.24 | High
GH8TAN54800A | FG5ANBD60L | 48 | 1400 | 72 | 95 | 53.12 | 27.04 | 3.6 | High
GH8TAN54800A | FG5ANBD60L | 48 | 1400 | 72 | 105 | 50.51 | 26.09 | 4.02 | High
GH8TAN54800A | FG5ANBD60L | 48 | 1400 | 67 | 75 | 52.57 | 34.59 | 2.91 | High
GH8TAN54800A | FG5ANBD60L | 48 | 1400 | 67 | 85 | 50.63 | 33.74 | 3.2 | High
GH8TAN54800A | FG5ANBD60L | 48 | 1400 | 67 | 95 | 47.9 | 33.08 | 3.56 | High
GH8TAN54800A | FG5ANBD60L | 48 | 1400 | 67 | 105 | 45.5 | 32.08 | 3.86 | High
GH8TAN54800A | FG5ANBD60L | 48 | 1400 | 62 | 75 | 47.28 | 41.82 | 2.88 | High
GH8TAN54800A | FG5ANBD60L | 48 | 1400 | 62 | 85 | 45.39 | 40.93 | 3.17 | High
GH8TAN54800A | FG5ANBD60L | 48 | 1400 | 62 | 95 | 43.37 | 39.97 | 3.54 | High
GH8TAN54800A | FG5ANBD60L | 48 | 1400 | 62 | 105 | 41.21 | 38.94 | 3.97 | High
GH8TAN54800A | FG5ANBD60L | 48 | 1600 | 72 | 75 | 59.33 | 29.89 | 3 | High
GH8TAN54800A | FG5ANBD60L | 48 | 1600 | 72 | 85 | 57.11 | 29.04 | 3.28 | High
GH8TAN54800A | FG5ANBD60L | 48 | 1600 | 72 | 95 | 54.68 | 28.11 | 3.63 | High
GH8TAN54800A | FG5ANBD60L | 48 | 1600 | 72 | 105 | 52.06 | 27.13 | 4.04 | High
GH8TAN54800A | FG5ANBD60L | 48 | 1600 | 67 | 75 | 53.77 | 36.64 | 2.95 | High
GH8TAN54800A | FG5ANBD60L | 48 | 1600 | 67 | 85 | 51.73 | 35.76 | 3.23 | High
GH8TAN54800A | FG5ANBD60L | 48 | 1600 | 67 | 95 | 49.5 | 34.8 | 3.59 | High
GH8TAN54800A | FG5ANBD60L | 48 | 1600 | 67 | 105 | 47.07 | 33.8 | 4.02 | High
GH8TAN54800A | FG5ANBD60L | 48 | 1600 | 62 | 75 | 48.65 | 43.19 | 2.91 | High
GH8TAN54800A | FG5ANBD60L | 48 | 1600 | 62 | 85 | 46.76 | 42.3 | 3.2 | High
GH8TAN54800A | FG5ANBD60L | 48 | 1600 | 62 | 95 | 44.71 | 41.32 | 3.57 | High
GH8TAN54800A | FG5ANBD60L | 48 | 1600 | 62 | 105 | 42.54 | 40.38 | 3.99 | High
GH8TAN56000A | FG5ANBD60L | 60 | 1750 | 72 | 75 | 69.58 | 36.55 | 3.8 | High
GH8TAN56000A | FG5ANBD60L | 60 | 1750 | 72 | 85 | 66.55 | 35.4 | 4.19 | High
GH8TAN56000A | FG5ANBD60L | 60 | 1750 | 72 | 95 | 63.29 | 34.18 | 4.64 | High
GH8TAN56000A | FG5ANBD60L | 60 | 1750 | 72 | 105 | 59.77 | 32.86 | 5.16 | High
GH8TAN56000A | FG5ANBD60L | 60 | 1750 | 67 | 75 | 63.19 | 45.28 | 3.76 | High
GH8TAN56000A | FG5ANBD60L | 60 | 1750 | 67 | 85 | 60.44 | 44.13 | 4.15 | High
GH8TAN56000A | FG5ANBD60L | 60 | 1750 | 67 | 95 | 57.5 | 42.9 | 4.6 | High
GH8TAN56000A | FG5ANBD60L | 60 | 1750 | 67 | 105 | 54.31 | 41.59 | 5.12 | High
GH8TAN56000A | FG5ANBD60L | 60 | 1750 | 62 | 75 | 57.67 | 53.81 | 3.73 | High
GH8TAN56000A | FG5ANBD60L | 60 | 1750 | 62 | 85 | 55.23 | 52.62 | 4.12 | High
GH8TAN56000A | FG5ANBD60L | 60 | 1750 | 62 | 95 | 52.64 | 51.32 | 4.57 | High
GH8TAN56000A | FG5ANBD60L | 60 | 1750 | 62 | 105 | 50.21 | 49.11 | 5.09 | High
GH8TAN56000A | FG5ANBD60L | 60 | 2000 | 72 | 75 | 70.8 | 38.4 | 3.89 | High
GH8TAN56000A | FG5ANBD60L | 60 | 2000 | 72 | 85 | 67.64 | 37.23 | 4.28 | High
GH8TAN56000A | FG5ANBD60L | 60 | 2000 | 72 | 95 | 64.24 | 35.98 | 4.73 | High
GH8TAN56000A | FG5ANBD60L | 60 | 2000 | 72 | 105 | 60.57 | 34.64 | 5.25 | High
GH8TAN56000A | FG5ANBD60L | 60 | 2000 | 67 | 75 | 64.37 | 48.33 | 3.85 | High
GH8TAN56000A | FG5ANBD60L | 60 | 2000 | 67 | 85 | 61.5 | 47.15 | 4.24 | High
GH8TAN56000A | FG5ANBD60L | 60 | 2000 | 67 | 95 | 58.44 | 45.9 | 4.69 | High
GH8TAN56000A | FG5ANBD60L | 60 | 2000 | 67 | 105 | 55.12 | 44.54 | 5.2 | High
GH8TAN56000A | FG5ANBD60L | 60 | 2000 | 62 | 75 | 59.1 | 57.82 | 3.82 | High
GH8TAN56000A | FG5ANBD60L | 60 | 2000 | 62 | 85 | 56.65 | 56.65 | 4.21 | High
GH8TAN56000A | FG5ANBD60L | 60 | 2000 | 62 | 95 | 54.22 | 54.22 | 4.66 | High
GH8TAN56000A | FG5ANBD60L | 60 | 2000 | 62 | 105 | 51.69 | 51.69 | 5.18 | High

## GH8_Heating
ODU_Model | IDU_Model | Size_Nom | Stage | EDB_F | CFM | ODB_F | Cap_Total_kBtu | Cap_Integ_kBtu | Sys_kW
GH8TAN52400A | FG5ANXB24L | 24 | High | 65 | 650 | -3 | 8.94 | 8.22 | 1.3
GH8TAN52400A | FG5ANXB24L | 24 | High | 65 | 650 | 7 | 11.48 | 10.55 | 1.37
GH8TAN52400A | FG5ANXB24L | 24 | High | 65 | 650 | 17 | 14.5 | 13.22 | 1.45
GH8TAN52400A | FG5ANXB24L | 24 | High | 65 | 650 | 27 | 17.42 | 15.47 | 1.52
GH8TAN52400A | FG5ANXB24L | 24 | High | 65 | 650 | 37 | 20.75 | 18.88 | 1.61
GH8TAN52400A | FG5ANXB24L | 24 | High | 65 | 650 | 47 | 24.63 | 24.63 | 1.72
GH8TAN52400A | FG5ANXB24L | 24 | High | 65 | 700 | -3 | 9.02 | 8.3 | 1.31
GH8TAN52400A | FG5ANXB24L | 24 | High | 65 | 700 | 7 | 11.58 | 10.65 | 1.37
GH8TAN52400A | FG5ANXB24L | 24 | High | 65 | 700 | 17 | 14.64 | 13.35 | 1.45
GH8TAN52400A | FG5ANXB24L | 24 | High | 65 | 700 | 27 | 17.54 | 15.58 | 1.52
GH8TAN52400A | FG5ANXB24L | 24 | High | 65 | 700 | 37 | 20.91 | 19.03 | 1.6
GH8TAN52400A | FG5ANXB24L | 24 | High | 65 | 700 | 47 | 24.82 | 24.82 | 1.7
GH8TAN52400A | FG5ANXB24L | 24 | High | 65 | 805 | -3 | 9.19 | 8.46 | 1.32
GH8TAN52400A | FG5ANXB24L | 24 | High | 65 | 805 | 7 | 11.73 | 10.78 | 1.38
GH8TAN52400A | FG5ANXB24L | 24 | High | 65 | 805 | 17 | 14.77 | 13.47 | 1.45
GH8TAN52400A | FG5ANXB24L | 24 | High | 65 | 805 | 27 | 17.76 | 15.77 | 1.51
GH8TAN52400A | FG5ANXB24L | 24 | High | 65 | 805 | 37 | 21.2 | 19.29 | 1.58
GH8TAN52400A | FG5ANXB24L | 24 | High | 65 | 805 | 47 | 25.16 | 25.16 | 1.68
GH8TAN52400A | FG5ANXB24L | 24 | High | 70 | 650 | -3 | 8.63 | 7.94 | 1.36
GH8TAN52400A | FG5ANXB24L | 24 | High | 70 | 650 | 7 | 11.14 | 10.24 | 1.43
GH8TAN52400A | FG5ANXB24L | 24 | High | 70 | 650 | 17 | 14.15 | 12.9 | 1.51
GH8TAN52400A | FG5ANXB24L | 24 | High | 70 | 650 | 27 | 17.22 | 15.3 | 1.6
GH8TAN52400A | FG5ANXB24L | 24 | High | 70 | 650 | 37 | 20.46 | 18.62 | 1.69
GH8TAN52400A | FG5ANXB24L | 24 | High | 70 | 650 | 47 | 24.26 | 24.26 | 1.8
GH8TAN52400A | FG5ANXB24L | 24 | High | 70 | 700 | -3 | 8.71 | 8.02 | 1.36
GH8TAN52400A | FG5ANXB24L | 24 | High | 70 | 700 | 7 | 11.24 | 10.33 | 1.43
GH8TAN52400A | FG5ANXB24L | 24 | High | 70 | 700 | 17 | 14.41 | 13.14 | 1.52
GH8TAN52400A | FG5ANXB24L | 24 | High | 70 | 700 | 27 | 17.33 | 15.39 | 1.59
GH8TAN52400A | FG5ANXB24L | 24 | High | 70 | 700 | 37 | 20.61 | 18.76 | 1.67
GH8TAN52400A | FG5ANXB24L | 24 | High | 70 | 700 | 47 | 24.46 | 24.46 | 1.78
GH8TAN52400A | FG5ANXB24L | 24 | High | 70 | 805 | -3 | 8.88 | 8.17 | 1.38
GH8TAN52400A | FG5ANXB24L | 24 | High | 70 | 805 | 7 | 11.43 | 10.5 | 1.44
GH8TAN52400A | FG5ANXB24L | 24 | High | 70 | 805 | 17 | 14.6 | 13.31 | 1.52
GH8TAN52400A | FG5ANXB24L | 24 | High | 70 | 805 | 27 | 17.53 | 15.57 | 1.58
GH8TAN52400A | FG5ANXB24L | 24 | High | 70 | 805 | 37 | 20.89 | 19.01 | 1.66
GH8TAN52400A | FG5ANXB24L | 24 | High | 70 | 805 | 47 | 24.8 | 24.8 | 1.76
GH8TAN52400A | FG5ANXB24L | 24 | High | 75 | 650 | -3 | 8.32 | 7.65 | 1.41
GH8TAN52400A | FG5ANXB24L | 24 | High | 75 | 650 | 7 | 10.82 | 9.94 | 1.49
GH8TAN52400A | FG5ANXB24L | 24 | High | 75 | 650 | 17 | 13.68 | 12.47 | 1.58
GH8TAN52400A | FG5ANXB24L | 24 | High | 75 | 650 | 27 | 16.97 | 15.07 | 1.67
GH8TAN52400A | FG5ANXB24L | 24 | High | 75 | 650 | 37 | 20.18 | 18.36 | 1.77
GH8TAN52400A | FG5ANXB24L | 24 | High | 75 | 650 | 47 | 23.91 | 23.91 | 1.89
GH8TAN52400A | FG5ANXB24L | 24 | High | 75 | 700 | -3 | 8.4 | 7.73 | 1.42
GH8TAN52400A | FG5ANXB24L | 24 | High | 75 | 700 | 7 | 10.91 | 10.03 | 1.49
GH8TAN52400A | FG5ANXB24L | 24 | High | 75 | 700 | 17 | 13.8 | 12.58 | 1.58
GH8TAN52400A | FG5ANXB24L | 24 | High | 75 | 700 | 27 | 17.08 | 15.17 | 1.66
GH8TAN52400A | FG5ANXB24L | 24 | High | 75 | 700 | 37 | 20.32 | 18.49 | 1.75
GH8TAN52400A | FG5ANXB24L | 24 | High | 75 | 700 | 47 | 24.1 | 24.1 | 1.87
GH8TAN52400A | FG5ANXB24L | 24 | High | 75 | 805 | -3 | 8.56 | 7.87 | 1.44
GH8TAN52400A | FG5ANXB24L | 24 | High | 75 | 805 | 7 | 11.1 | 10.2 | 1.5
GH8TAN52400A | FG5ANXB24L | 24 | High | 75 | 805 | 17 | 14.03 | 12.79 | 1.58
GH8TAN52400A | FG5ANXB24L | 24 | High | 75 | 805 | 27 | 17.29 | 15.35 | 1.66
GH8TAN52400A | FG5ANXB24L | 24 | High | 75 | 805 | 37 | 20.59 | 18.74 | 1.74
GH8TAN52400A | FG5ANXB24L | 24 | High | 75 | 805 | 47 | 24.44 | 24.44 | 1.84
GH8TAN53600A | FG5ANXC36L | 36 | High | 65 | 975 | -3 | 15.26 | 14.03 | 2.08
GH8TAN53600A | FG5ANXC36L | 36 | High | 65 | 975 | 7 | 19.03 | 17.48 | 2.21
GH8TAN53600A | FG5ANXC36L | 36 | High | 65 | 975 | 17 | 23.28 | 21.23 | 2.35
GH8TAN53600A | FG5ANXC36L | 36 | High | 65 | 975 | 27 | 27.38 | 24.32 | 2.49
GH8TAN53600A | FG5ANXC36L | 36 | High | 65 | 975 | 37 | 32.04 | 29.16 | 2.65
GH8TAN53600A | FG5ANXC36L | 36 | High | 65 | 975 | 47 | 37.3 | 37.3 | 2.85
GH8TAN53600A | FG5ANXC36L | 36 | High | 65 | 1050 | -3 | 15.39 | 14.16 | 2.09
GH8TAN53600A | FG5ANXC36L | 36 | High | 65 | 1050 | 7 | 19.18 | 17.63 | 2.21
GH8TAN53600A | FG5ANXC36L | 36 | High | 65 | 1050 | 17 | 23.41 | 21.34 | 2.35
GH8TAN53600A | FG5ANXC36L | 36 | High | 65 | 1050 | 27 | 27.55 | 24.47 | 2.48
GH8TAN53600A | FG5ANXC36L | 36 | High | 65 | 1050 | 37 | 32.25 | 29.35 | 2.64
GH8TAN53600A | FG5ANXC36L | 36 | High | 65 | 1050 | 47 | 37.55 | 37.55 | 2.82
GH8TAN53600A | FG5ANXC36L | 36 | High | 65 | 1205 | -3 | 15.65 | 14.39 | 2.12
GH8TAN53600A | FG5ANXC36L | 36 | High | 65 | 1205 | 7 | 19.5 | 17.92 | 2.23
GH8TAN53600A | FG5ANXC36L | 36 | High | 65 | 1205 | 17 | 23.68 | 21.59 | 2.36
GH8TAN53600A | FG5ANXC36L | 36 | High | 65 | 1205 | 27 | 27.86 | 24.75 | 2.48
GH8TAN53600A | FG5ANXC36L | 36 | High | 65 | 1205 | 37 | 32.63 | 29.69 | 2.63
GH8TAN53600A | FG5ANXC36L | 36 | High | 65 | 1205 | 47 | 38 | 38 | 2.8
GH8TAN53600A | FG5ANXC36L | 36 | High | 70 | 975 | -3 | 14.82 | 13.64 | 2.17
GH8TAN53600A | FG5ANXC36L | 36 | High | 70 | 975 | 7 | 18.58 | 17.07 | 2.3
GH8TAN53600A | FG5ANXC36L | 36 | High | 70 | 975 | 17 | 23.01 | 20.98 | 2.46
GH8TAN53600A | FG5ANXC36L | 36 | High | 70 | 975 | 27 | 27.05 | 24.03 | 2.61
GH8TAN53600A | FG5ANXC36L | 36 | High | 70 | 975 | 37 | 31.64 | 28.79 | 2.77
GH8TAN53600A | FG5ANXC36L | 36 | High | 70 | 975 | 47 | 36.81 | 36.81 | 2.97
GH8TAN53600A | FG5ANXC36L | 36 | High | 70 | 1050 | -3 | 14.96 | 13.76 | 2.18
GH8TAN53600A | FG5ANXC36L | 36 | High | 70 | 1050 | 7 | 18.73 | 17.21 | 2.31
GH8TAN53600A | FG5ANXC36L | 36 | High | 70 | 1050 | 17 | 23.14 | 21.1 | 2.46
GH8TAN53600A | FG5ANXC36L | 36 | High | 70 | 1050 | 27 | 27.22 | 24.17 | 2.6
GH8TAN53600A | FG5ANXC36L | 36 | High | 70 | 1050 | 37 | 31.84 | 28.97 | 2.76
GH8TAN53600A | FG5ANXC36L | 36 | High | 70 | 1050 | 47 | 37.06 | 37.06 | 2.95
GH8TAN53600A | FG5ANXC36L | 36 | High | 70 | 1205 | -3 | 15.21 | 13.99 | 2.21
GH8TAN53600A | FG5ANXC36L | 36 | High | 70 | 1205 | 7 | 19.02 | 17.48 | 2.33
GH8TAN53600A | FG5ANXC36L | 36 | High | 70 | 1205 | 17 | 23.4 | 21.34 | 2.47
GH8TAN53600A | FG5ANXC36L | 36 | High | 70 | 1205 | 27 | 27.52 | 24.44 | 2.59
GH8TAN53600A | FG5ANXC36L | 36 | High | 70 | 1205 | 37 | 32.21 | 29.31 | 2.74
GH8TAN53600A | FG5ANXC36L | 36 | High | 70 | 1205 | 47 | 37.5 | 37.5 | 2.92
GH8TAN53600A | FG5ANXC36L | 36 | High | 75 | 975 | -3 | 14.37 | 13.22 | 2.26
GH8TAN53600A | FG5ANXC36L | 36 | High | 75 | 975 | 7 | 18.14 | 16.67 | 2.4
GH8TAN53600A | FG5ANXC36L | 36 | High | 75 | 975 | 17 | 22.74 | 20.73 | 2.58
GH8TAN53600A | FG5ANXC36L | 36 | High | 75 | 975 | 27 | 26.73 | 23.74 | 2.73
GH8TAN53600A | FG5ANXC36L | 36 | High | 75 | 975 | 37 | 31.24 | 28.43 | 2.9
GH8TAN53600A | FG5ANXC36L | 36 | High | 75 | 975 | 47 | 36.32 | 36.32 | 3.11
GH8TAN53600A | FG5ANXC36L | 36 | High | 75 | 1050 | -3 | 14.51 | 13.35 | 2.27
GH8TAN53600A | FG5ANXC36L | 36 | High | 75 | 1050 | 7 | 18.29 | 16.81 | 2.41
GH8TAN53600A | FG5ANXC36L | 36 | High | 75 | 1050 | 17 | 22.88 | 20.86 | 2.58
GH8TAN53600A | FG5ANXC36L | 36 | High | 75 | 1050 | 27 | 26.89 | 23.88 | 2.72
GH8TAN53600A | FG5ANXC36L | 36 | High | 75 | 1050 | 37 | 31.43 | 28.6 | 2.88
GH8TAN53600A | FG5ANXC36L | 36 | High | 75 | 1050 | 47 | 36.57 | 36.57 | 3.08
GH8TAN53600A | FG5ANXC36L | 36 | High | 75 | 1205 | -3 | 14.77 | 13.59 | 2.3
GH8TAN53600A | FG5ANXC36L | 36 | High | 75 | 1205 | 7 | 18.57 | 17.07 | 2.42
GH8TAN53600A | FG5ANXC36L | 36 | High | 75 | 1205 | 17 | 23.13 | 21.09 | 2.58
GH8TAN53600A | FG5ANXC36L | 36 | High | 75 | 1205 | 27 | 27.18 | 24.14 | 2.71
GH8TAN53600A | FG5ANXC36L | 36 | High | 75 | 1205 | 37 | 31.79 | 28.93 | 2.87
GH8TAN53600A | FG5ANXC36L | 36 | High | 75 | 1205 | 47 | 37 | 37 | 3.05
GH8TAN54800A | FG5ANBD60L | 48 | High | 65 | 1300 | -3 | 20.66 | 19 | 2.63
GH8TAN54800A | FG5ANBD60L | 48 | High | 65 | 1300 | 7 | 25.6 | 23.53 | 2.77
GH8TAN54800A | FG5ANBD60L | 48 | High | 65 | 1300 | 17 | 31.31 | 28.54 | 2.93
GH8TAN54800A | FG5ANBD60L | 48 | High | 65 | 1300 | 27 | 37.04 | 32.9 | 3.08
GH8TAN54800A | FG5ANBD60L | 48 | High | 65 | 1300 | 37 | 42.67 | 38.83 | 3.25
GH8TAN54800A | FG5ANBD60L | 48 | High | 65 | 1300 | 47 | 48.81 | 48.81 | 3.45
GH8TAN54800A | FG5ANBD60L | 48 | High | 65 | 1400 | -3 | 20.87 | 19.2 | 2.64
GH8TAN54800A | FG5ANBD60L | 48 | High | 65 | 1400 | 7 | 25.84 | 23.74 | 2.77
GH8TAN54800A | FG5ANBD60L | 48 | High | 65 | 1400 | 17 | 32.06 | 29.23 | 2.93
GH8TAN54800A | FG5ANBD60L | 48 | High | 65 | 1400 | 27 | 37.26 | 33.1 | 3.06
GH8TAN54800A | FG5ANBD60L | 48 | High | 65 | 1400 | 37 | 42.95 | 39.09 | 3.21
GH8TAN54800A | FG5ANBD60L | 48 | High | 65 | 1400 | 47 | 49.16 | 49.16 | 3.4
GH8TAN54800A | FG5ANBD60L | 48 | High | 65 | 1600 | -3 | 21.25 | 19.55 | 2.66
GH8TAN54800A | FG5ANBD60L | 48 | High | 65 | 1600 | 7 | 26.26 | 24.13 | 2.78
GH8TAN54800A | FG5ANBD60L | 48 | High | 65 | 1600 | 17 | 32.44 | 29.58 | 2.92
GH8TAN54800A | FG5ANBD60L | 48 | High | 65 | 1600 | 27 | 37.67 | 33.46 | 3.04
GH8TAN54800A | FG5ANBD60L | 48 | High | 65 | 1600 | 37 | 43.47 | 39.56 | 3.18
GH8TAN54800A | FG5ANBD60L | 48 | High | 65 | 1600 | 47 | 49.75 | 49.75 | 3.34
GH8TAN54800A | FG5ANBD60L | 48 | High | 70 | 1300 | -3 | 19.76 | 18.18 | 2.75
GH8TAN54800A | FG5ANBD60L | 48 | High | 70 | 1300 | 7 | 24.79 | 22.78 | 2.9
GH8TAN54800A | FG5ANBD60L | 48 | High | 70 | 1300 | 17 | 30.34 | 27.66 | 3.06
GH8TAN54800A | FG5ANBD60L | 48 | High | 70 | 1300 | 27 | 36.54 | 32.46 | 3.25
GH8TAN54800A | FG5ANBD60L | 48 | High | 70 | 1300 | 37 | 42.11 | 38.32 | 3.41
GH8TAN54800A | FG5ANBD60L | 48 | High | 70 | 1300 | 47 | 48.16 | 48.16 | 3.62
GH8TAN54800A | FG5ANBD60L | 48 | High | 70 | 1400 | -3 | 19.96 | 18.37 | 2.76
GH8TAN54800A | FG5ANBD60L | 48 | High | 70 | 1400 | 7 | 25.01 | 22.99 | 2.9
GH8TAN54800A | FG5ANBD60L | 48 | High | 70 | 1400 | 17 | 30.6 | 27.9 | 3.05
GH8TAN54800A | FG5ANBD60L | 48 | High | 70 | 1400 | 27 | 36.76 | 32.65 | 3.22
GH8TAN54800A | FG5ANBD60L | 48 | High | 70 | 1400 | 37 | 42.38 | 38.57 | 3.38
GH8TAN54800A | FG5ANBD60L | 48 | High | 70 | 1400 | 47 | 48.5 | 48.5 | 3.57
GH8TAN54800A | FG5ANBD60L | 48 | High | 70 | 1600 | -3 | 20.33 | 18.71 | 2.78
GH8TAN54800A | FG5ANBD60L | 48 | High | 70 | 1600 | 7 | 25.43 | 23.37 | 2.91
GH8TAN54800A | FG5ANBD60L | 48 | High | 70 | 1600 | 17 | 31.09 | 28.35 | 3.04
GH8TAN54800A | FG5ANBD60L | 48 | High | 70 | 1600 | 27 | 37.16 | 33.01 | 3.19
GH8TAN54800A | FG5ANBD60L | 48 | High | 70 | 1600 | 37 | 42.85 | 39 | 3.33
GH8TAN54800A | FG5ANBD60L | 48 | High | 70 | 1600 | 47 | 49.08 | 49.08 | 3.51
GH8TAN54800A | FG5ANBD60L | 48 | High | 75 | 1300 | -3 | 18.84 | 17.33 | 2.88
GH8TAN54800A | FG5ANBD60L | 48 | High | 75 | 1300 | 7 | 23.98 | 22.04 | 3.04
GH8TAN54800A | FG5ANBD60L | 48 | High | 75 | 1300 | 17 | 29.54 | 26.94 | 3.21
GH8TAN54800A | FG5ANBD60L | 48 | High | 75 | 1300 | 27 | 36.1 | 32.07 | 3.42
GH8TAN54800A | FG5ANBD60L | 48 | High | 75 | 1300 | 37 | 41.58 | 37.84 | 3.59
GH8TAN54800A | FG5ANBD60L | 48 | High | 75 | 1300 | 47 | 47.53 | 47.53 | 3.8
GH8TAN54800A | FG5ANBD60L | 48 | High | 75 | 1400 | -3 | 19.04 | 17.52 | 2.89
GH8TAN54800A | FG5ANBD60L | 48 | High | 75 | 1400 | 7 | 24.2 | 22.24 | 3.04
GH8TAN54800A | FG5ANBD60L | 48 | High | 75 | 1400 | 17 | 29.79 | 27.16 | 3.2
GH8TAN54800A | FG5ANBD60L | 48 | High | 75 | 1400 | 27 | 36.29 | 32.23 | 3.39
GH8TAN54800A | FG5ANBD60L | 48 | High | 75 | 1400 | 37 | 41.83 | 38.06 | 3.56
GH8TAN54800A | FG5ANBD60L | 48 | High | 75 | 1400 | 47 | 47.87 | 47.87 | 3.75
GH8TAN54800A | FG5ANBD60L | 48 | High | 75 | 1600 | -3 | 19.41 | 17.86 | 2.91
GH8TAN54800A | FG5ANBD60L | 48 | High | 75 | 1600 | 7 | 24.59 | 22.6 | 3.05
GH8TAN54800A | FG5ANBD60L | 48 | High | 75 | 1600 | 17 | 30.25 | 27.58 | 3.19
GH8TAN54800A | FG5ANBD60L | 48 | High | 75 | 1600 | 27 | 36.66 | 32.56 | 3.36
GH8TAN54800A | FG5ANBD60L | 48 | High | 75 | 1600 | 37 | 42.28 | 38.48 | 3.51
GH8TAN54800A | FG5ANBD60L | 48 | High | 75 | 1600 | 47 | 48.42 | 48.42 | 3.68

## Valid_Combinations
ODU_Model | ODU_Series | ODU_Stage | IDU_Model_Pattern | IDU_Series | Nom_Tons | Nom_kBtu | Cooling_Mode | Heating_Mode | Notes
GA5SAN51800W | GA5SAN5 | 1-Stage | FJ5AN*A18L* | FJ5 | 1.5 | 18 | Yes | No | Single-stage A/C cooling only
GA5SAN52400W | GA5SAN5 | 1-Stage | FJ5AN*B24L* | FJ5 | 2 | 24 | Yes | No | Single-stage A/C cooling only
GA5SAN53000W | GA5SAN5 | 1-Stage | FJ5AN*B30L* | FJ5 | 2.5 | 30 | Yes | No | Single-stage A/C cooling only
GA5SAN53602W | GA5SAN5 | 1-Stage | FJ5AN*B36L* | FJ5 | 3 | 36 | Yes | No | Single-stage A/C cooling only
GA5SAN54201W | GA5SAN5 | 1-Stage | FJ5AN*C42L* | FJ5 | 3.5 | 42 | Yes | No | Single-stage A/C cooling only
GA5SAN54801W | GA5SAN5 | 1-Stage | FJ5AN*C48L* | FJ5 | 4 | 48 | Yes | No | Single-stage A/C cooling only
GA5SAN56000W | GA5SAN5 | 1-Stage | FJ5AN*D60L* | FJ5 | 5 | 60 | Yes | No | Single-stage A/C cooling only
GA8TAN52400W | GA8TAN5 | 2-Stage | FG5ANXB24L* | FG5 | 2 | 24 | Yes | No | 2-stage A/C; use High stage for peak load selection
GA8TAN53600W | GA8TAN5 | 2-Stage | FG5ANXC36L* | FG5 | 3 | 36 | Yes | No | 2-stage A/C; use High stage for peak load selection
GA8TAN54800W | GA8TAN5 | 2-Stage | FG5ANBD60L* | FG5 | 4 | 48 | Yes | No | 2-stage A/C; use High stage for peak load selection
GA8TAN56000W | GA8TAN5 | 2-Stage | FG5ANBD60L* | FG5 | 5 | 60 | Yes | No | 2-stage A/C; use High stage for peak load selection
GH5SAN51800A | GH5SAN5 | 1-Stage | FJ5AN*A18L* | FJ5 | 1.5 | 18 | Yes | Yes | Single-stage HP; max heat ODB -10F, max cool ODB 125F
GH5SAN52400A | GH5SAN5 | 1-Stage | FJ5AN*B24L* | FJ5 | 2 | 24 | Yes | Yes | Single-stage HP
GH5SAN53000A | GH5SAN5 | 1-Stage | FJ5AN*B30L* | FJ5 | 2.5 | 30 | Yes | Yes | Single-stage HP
GH5SAN53600A | GH5SAN5 | 1-Stage | FJ5AN*B36L* | FJ5 | 3 | 36 | Yes | Yes | Single-stage HP
GH5SAN54200A | GH5SAN5 | 1-Stage | FJ5AN*C42L* | FJ5 | 3.5 | 42 | Yes | Yes | Single-stage HP
GH5SAN54800A | GH5SAN5 | 1-Stage | FJ5AN*C48L* | FJ5 | 4 | 48 | Yes | Yes | Single-stage HP
GH5SAN56000A | GH5SAN5 | 1-Stage | FJ5AN*D60L* | FJ5 | 5 | 60 | Yes | Yes | Single-stage HP
GH8TAN52400A | GH8TAN5 | 2-Stage | FG5ANXB24L* | FG5 | 2 | 24 | Yes | Yes | 2-stage HP; min heat ODB -8F; use High stage for peak
GH8TAN53600A | GH8TAN5 | 2-Stage | FG5ANXC36L* | FG5 | 3 | 36 | Yes | Yes | 2-stage HP
GH8TAN54800A | GH8TAN5 | 2-Stage | FG5ANBD60L* | FG5 | 4 | 48 | Yes | Yes | 2-stage HP
GH8TAN56000A | GH8TAN5 | 2-Stage | FG5ANBD60L* | FG5 | 5 | 60 | Yes | Yes | 2-stage HP

## SHC_Correction
SHC Correction Factor for Entering DB ≠ 80°F
Formula:
Correction Factor CF = 1.09 × (1 - BF) × (EDB - 80)
Application:
If EDB < 80°F: SHC_corrected = SHC_table - (CF × CFM)
If EDB > 80°F: SHC_corrected = SHC_table + (CF × CFM)
Quick-reference correction per degree from 80°F at given BF:
BF = 0.00: CF = 1.090 per °F
BF = 0.10: CF = 0.981 per °F
BF = 0.20: CF = 0.872 per °F
BF = 0.30: CF = 0.763 per °F
Note: BF = 0 in table means no psychrometric solution — use BF of next lower EWB.
Sensible correction for GA5/GA8 detailed tables:
Deduct 835 Btuh per 1000 CFM per °F below 80°F EDB
Add 835 Btuh per 1000 CFM per °F above 80°F EDB

## FG5_Airflow
FC_Size | ODU_Size_kBtu | A/C_Cool_Nom_CFM | A/C_Cool_Dehum_CFM | HP_Comfort_CFM | HP_Efficiency_CFM | Source: FG5 Table 5 (Cooling Mode) & Table 7 (HP Heating). Nominal CFM shown.
24 | 18 | 525 | 420 | 470 | 525
24 | 24 | 700 | 560 | 630 | 700
24 | 30 | 875 | 700 | 785 | 875
24 | 36 | 1050 | 840 | 945 | 1050
36 | 24 | 700 | 560 | 630 | 700
36 | 30 | 875 | 700 | 785 | 875
36 | 36 | 1050 | 840 | 945 | 1050
36 | 42 | 1225 | 980 | 1100 | 1225
48 | 30 | 875 | 700 | 785 | 875
48 | 36 | 1050 | 840 | 945 | 1050
48 | 42 | 1225 | 980 | 1100 | 1225
48 | 48 | 1400 | 1120 | 1260 | 1400
60 | 36 | 1050 | 840 | 945 | 1050
60 | 42 | 1225 | 980 | 1100 | 1225
60 | 48 | 1400 | 1120 | 1260 | 1400
60 | 60 | 1750 | 1400 | 1575 | 1750

## FJ5_Airflow
FC_Size | Nom_CFM | Tap5_0.2inESP | Tap5_0.4inESP | Tap5_0.6inESP | Tap4_0.2inESP | Tap3_0.2inESP | Min_Heater_CFM_10kW | Source: FJ5 Table 4 (Wet). Tap5 shown for primary CFM. Tap 4/3 are same on sizes 18-48. Min CFM for 10kW heater shown.
18 | 525 | 737 | 694 | 641 | 678 | 678 | 600
24 | 700 | 1003 | 925 | 838 | 907 | 907 | 700
30 | 875 | 1215 | 1154 | 1083 | 1114 | 1114 | 875
36 | 1050 | 1404 | 1328 | 1251 | 1277 | 1277 | 970
42 | 1225 | 1551 | 1473 | 1407 | 1493 | 1493 | 1225
48 | 1400 | 1853 | 1795 | 1737 | 1673 | 1673 | 1400
60 | 1750 | 2067 | 1996 | 1928 | 2067 | 2067 | 1750